## Release Notes
DGA900 Plus Register Map - Release Notes
Objective:
This document describes updates to the Modbus, DNP3 and IEC61850 data mapping within the DGA900 Plus product.
Compatability
Revision number | DGA900 Plus FW | Kalkitech FW | Kalkitech .ecc | EasyConnect SW
1.0.0 | 4.48.1 | 4.15.3 | DGA900_Family_P_DNP3_v2.0.1.ecc DGA900_Family_P_IEC61850_Ed2_v2.0.2.ecc DGA900_Family_P_IEC61850_Ed1_v1.0.2ecc | 6.15.3
Revision History
Rev Number | Author | Release Date | Change Description | Approved by
1.0.0 | Rajasekhar Musinada | 2024-05-20 | 1. Analog input mapped Top temperature measurement registers are added in BMT 2. Frequency alarm limit and hystersis registers are added in BMT 3. Channel-wise temperature measurement registers are removed in BMT 4. Channel-wise polar plots for power factor & C1 registers are removed in BMT 5. Data template of IEC 61850 IID files is revised with extended logical nodes | Rajasekhar Musinada
Important Note | 1. Customers using BMToption in DGA900 Plus must be careful about BMT registers mapping as few of the invalid registers have been depricated. 2. Data template in IEC61850 IID files have been revised. Please go through the new register mapping in DGA900 Plus sheet before upgrading

## Instructions
DGA900 Plus Register Map
Objective:
This document describes the Modbus,DNP3 and IEC61850 data mapping within the DGA900 Plus product.
Instructions
Filters can be applied to hide cells that are not applicable.
Modbus
Table 1 shows an example of the Modbus register information. Modbus address = modbus address. Description = description of the register. Data type = Format of the modbus data (Boolean, Integer, Float etc). Range = effective range of the measurements. Scaling = The scaling factor applied to the mesurements. Modbus address Some Modbus systems represent the addressing starting at 1. That’s the way DGA900 Plus products were developed. Other Modbus systems may start at 0. DGA900 Plus products starts addressing by 1. For those systems with addressing start from 0 you should subtract 1 from all the register index as indicated in DGA900 Plus Modbus point mapping. Note: Users can select Modbus registers starting value (0 or 1) using a dropdown option in the cell at the top of Modbus section in DGA900 Plus page. Data Format The MODBUS specification only defines commands to read and write 16-bit integer values. However these commands can be used to read other data formats. DGA900 Plus devices registers can store character strings, bit fields, floating point values, IP addresses, dates, time and phone numbers. These are all read as integers using the MODBUS commands, and must be correctly interpreted by the master device. It is anticipated that not all MODBUS masters will be able to correctly interpret non-integer data, so the main critical data (current measurement details) have been duplicated in both integer and floating point format. DGA900 Plus uses DISCRETE INPUTS function only to read digital values and INPUT REGISTER function only to read analog values. Digital values are available directly as discrete values with no need to parse. Strings Character strings are simple fixed length 8-bit ASCII strings, where each MODBUS 16-bit integer contains two ASCII characters. DGA900 Plus devices use multiple words of 16-bit integer. If a string with an odd number of characters is required, the last word must be padded with a NULL character . For the ASCII table: http://www.asciitable.com/ Example: Input register 1000: value 0x5458 àmeans “TX” Bit Fields Bit fields are used repeatedly for various configuration registers. These are detailed in the Bit Fields sheet on the variables mapping. ENDIANNESS All data In DGA900 Plus Modbus implementation is formatted in Big Endian (Network) order. Most systems use big endian. For understanding big endian and little endian: http://en.wikipedia.org/wiki/Endianness Example: 0x0A0B0C0D From Wikipedia: “If you are writing in a western language the hex value 0x0a0b0c0d you are writing the bytes from left to right, you are implicitly writing Big-Endian style. 0x0a at 0, 0x0b at 1, 0x0c at 2, 0x0d at 3. On the other hand the output of memory is normally also printed out bytewise from left to right, first memory address 0, then memory address 1, then memory address 2, then memory address 3. So on a Big-Endian system when you write a 32-bit value (from a register) to an address in memory and after that output the memory, you "see what you have written" (because you are using the left to right coordinate system for the output of values in registers as well as the output of memory).”
Modbus Address | Description | Data Type | Range | Scaling | Available in Modbus
11000 | BM Set1 Power Frequency (Hz) | FLOAT32 | 45-65 Hz | 1
Table 1
DNP Objects and Points
Table 2 shows an example of the the DNP3 data point information. Available in DNP3 = A tick is added to this box if the register is available in the DNP3 map. DNP Object = The DNP Object of the register (1 - Binary Input, 30 - Analog Input). DNP Point Index = The DNP address of the single data value of the type specified by the DNP Object. Class Assigned = The class assigned to the data point. Static Variation = The Static Variation of the data point. Event Variation = The Event Variation of the data point. Native Default Status = Active if the register is enabled by default in the Native DNP3 profile.
Available in DNP3 | DNP Object | DNP Point Index | Class Assigned | Static Variation | Event Variation | Native Default Status
| 1 | 0 | 1 | 1 | 2 | Active
Table 2
DNP3 ENUMERATION
DGA scheduler mode
Output | Mode
0 | Normal Mode
1 | Caution Mode
2 | Alarm Mode
3 | Suspended Mode
GE Binary Date Format
Format | Description
MMDDYYYY (hex) | MM = Month from 1 to 12 in Binary format
DD = Day from 1 to 31 in Binary format
YYYY = Year, Binary format (valid range from 1990 to 2089)
GE Binary Time Format
Format | Description
HHMMSSSS (hex) | HH = Hours from 0 to 23 in Binary format
MM = Minutes from 0 to 59 in Binary format
SSSS = Seconds from 0 to 59 and milliseconds from 0 to 999 in Binary format.
(0x0000=00.000 sec, 0x0001=00.001 sec, …, 0xEA5F (or 59999) = 59.999 sec)
PGA Error Codes
Bit | Description
31 | 1 = Timeout
30 | 1 = Conditioned oil temp. outside limits
29 | 1 = Drain level shows oil
28 | 1 = Temperature Sensor(s) 2 disconnected
27 | 1 = Temperature Sensor(s) 1 disconnected
26 | not used
25 | 1 = Oil pump not turning
24 | 1 = Oil pump tacho count too low
23 | 1 = Manual oil sampling switch
22 | 1 = Oil pump speed out of range
21 | 1 = Oil pump pressure too low
20 | 1 = Oil pump tacho count too high
19 | 1 = Oil pressure too high
18 | 1 = Oil pressure too low
17 | 1 = Oil temperature too high
16 | 1 = Oil temperature too low
15 | 1 = Unusual ambient gas measurements
14 | 1 = Gas leak test: Pressure decay too high
13 | 1 = Gas leak test: Pump pressure too low
12 | 1 = Bad communication with controlboard
11 | 1 = PGA Air temperature outside limits
10 | 1 = Over Fill level shows oil
9 | 1 = Fill level shows oil
8 | 1 = No Levelsensor3 signal (oil drain)
7 | 1 = No levelsensor1 signal (oil level)
6 | 1 = Microphone test failed
5 | 1 = Background noise/vibration too high
4 | 1 = Gas flow lower than limit
3 | 1 = PGA IR-source outside range
2 | 1 = PGA chopper frequency outside range
1 | 1 = PGA power supply voltage too low
0 | 1 = Missing mains input
Measurement Flags
Bit | Description
15 | 1 = TDH Valid
14 | 1 = External Alarm ON
13 | 1 = Measured with PreSens
12 | 1 = Strong NHC Indication
11 | 1 = Weak NHC Indication
10 | 1 = Measurement Manually Stopped
9 | 1 = Manual Sample
8 | 1 = Spurious alarm suspected
7 | 1 = Oil switch failed
6 | 1 = TDG valid
5 | 1 = Nitrogen valid
4 | 1 = Error checking disabled
3 | 1 = Sampling skipped
2 | 1 = First measurement after reset
1 | 1 = PPM values are valid
0 | 1 = ESHL Valid
Host Firmware Format
Format | Description
MMMMmmRR (hex) | MMMM = Firmware major version, Binary format
mm = Firmware minor version, Binary format
RR = Firmware revision, Binary format
IEC61850
Table 3 shows an example of the IEC61850 tag information. Available in IEC61850 = A tick is added to this box if the register is available in the IEC61850 map. Logical Device = Name of the logical device present in ICD file Logical Node = Instance of the logical node of logical device Function = Functional constraint of the data object Data Object = Instance of the data object of logical node Sub Data Object = Instance of the sub data object if any exists. Attribute = Attribute of an instanciated data object IED Tag = Unique ID to access the data point
Available in IEC61850 | Logical Device | Logical Node | Function | Data Object | Sub Data Object | Attribute | Attribute 2 | IED Tag
| BMT | GGIO1 | ST | DoorWrn |  | stVal |  | BMT$GGIO1$ST$DoorWrn$stVal
Table 3
KALKI MODULE DEFAULT CONFIGURATION
The Kalkitech Sync 261 has 2 ethernet ports as shown in Figure.
Table 4 lists the default configuration values for the eth0 port.
Description | Value
IP Address | 192.168.0.121
Mask | 255.255.255.0
Gateway | 192.168.0.1
Table 4
Table 5 lists the default configuration values for the eth1 port.
Description | Value
IP Address | 192.168.1.121
Mask | 255.255.255.0
Gateway | 192.168.1.1
Table 5

## DGA900 Plus
DGA900 Plus |  |  | MODBUS | Customer Modbus Registers |  |  | DNP3 | [7 empty] | IEC 61850
|  |  | Click + é to | Numbering Starting by: |  | 0 | Click + é to | [7 empty] | Click + é to
Product |  |  | Expand |  | (select the Blue cell)é |  | Expand | [7 empty] | Expand
Description | Point Association | Range |  | Modbus Address | Data Type | Scaling |  | DNP Object | DNP Point Index | Class Assigned | Static Variation | Event Variation | Available in DNP3 | Native Default Status |  | Logical Device | Logical Node | Functional Constraint | Data Object | Sub Data Object | Attribute | Attribute 2 | IED Tag | Available in IEC61850 | Alias | Modbus Native Address
Caution Indicator Status | General | N/A | 0 | 999 | BOOLEAN | N/A |  | 1 | 0 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | Caution |  | stVal |  | OS/GGIO1$ST$Caution$stVal | ✔ | caution_ind_of | 1000
Alarm Indicator Status | General | N/A | 1 | 1000 | BOOLEAN | N/A |  | 1 | 1 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | Alarm |  | stVal |  | OS/GGIO1$ST$Alarm$stVal | ✔ | alarm_ind_of | 1001
Service Indicator Status | General | N/A |  | 1001 | BOOLEAN | N/A |  | 1 | 2 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | Service |  | stVal |  | OS/GGIO1$ST$Service$stVal | ✔ | service_ind_of | 1002
Relay 1 Status | General | N/A |  | 1002 | BOOLEAN | N/A |  | 1 | 3 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | Relay1 |  | stVal |  | OS/GGIO1$ST$Relay1$stVal | ✔ | relay1_of | 1003
Relay 2 Status | General | N/A |  | 1003 | BOOLEAN | N/A |  | 1 | 4 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | Relay2 |  | stVal |  | OS/GGIO1$ST$Relay2$stVal | ✔ | relay2_of | 1004
Relay 3 Status | General | N/A |  | 1004 | BOOLEAN | N/A |  | 1 | 5 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | Relay3 |  | stVal |  | OS/GGIO1$ST$Relay3$stVal | ✔ | relay3_of | 1005
Relay 4 Status | General | N/A |  | 1005 | BOOLEAN | N/A |  | 1 | 6 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | Relay4 |  | stVal |  | OS/GGIO1$ST$Relay4$stVal | ✔ | relay4_of | 1006
Relay 5 Status | General | N/A |  | 1006 | BOOLEAN | N/A |  | 1 | 7 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | Relay5 |  | stVal |  | OS/GGIO1$ST$Relay5$stVal | ✔ | relay5_of | 1007
Relay 6 Status | General | N/A |  | 1007 | BOOLEAN | N/A |  | 1 | 8 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | Relay6 |  | stVal |  | OS/GGIO1$ST$Relay6$stVal | ✔ | relay6_of | 1008
Relay 7 Status | General | N/A |  | 1008 | BOOLEAN | N/A |  | 1 | 9 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | Relay7 |  | stVal |  | OS/GGIO1$ST$Relay7$stVal | ✔ | relay7_of | 1009
Source 1 H2 High-High Alarm | Source 1 | N/A |  | 1009 | BOOLEAN | N/A |  | 1 | 10 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | H2Alm |  | stVal |  | OS/SIML1$ST$H2Alm$stVal | ✔ | source_1__h2__high_high__alarm | 1010
Source 1 H2 High Alarm | Source 1 | N/A |  | 1010 | BOOLEAN | N/A |  | 1 | 11 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | H2Wrn |  | stVal |  | OS/SIML1$ST$H2Wrn$stVal | ✔ | source_1__h2__high__alarm | 1011
Source 1 CO2 High-High Alarm | Source 1 | N/A |  | 1011 | BOOLEAN | N/A |  | 1 | 12 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | CO2Alm |  | stVal |  | OS/SIML1$ST$CO2Alm$stVal | ✔ | source_1__co2__high_high__alarm | 1012
Source 1 CO2 High Alarm | Source 1 | N/A |  | 1012 | BOOLEAN | N/A |  | 1 | 13 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | CO2Wrn |  | stVal |  | OS/SIML1$ST$CO2Wrn$stVal | ✔ | source_1__co2__high__alarm | 1013
Source 1 CO High-High Alarm | Source 1 | N/A |  | 1013 | BOOLEAN | N/A |  | 1 | 14 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | COAlm |  | stVal |  | OS/SIML1$ST$COAlm$stVal | ✔ | source_1__co__high_high__alarm | 1014
Source 1 CO High Alarm | Source 1 | N/A |  | 1014 | BOOLEAN | N/A |  | 1 | 15 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | COWrn |  | stVal |  | OS/SIML1$ST$COWrn$stVal | ✔ | source_1__co__high__alarm | 1015
Source 1 C2H4 High-High Alarm | Source 1 | N/A |  | 1015 | BOOLEAN | N/A |  | 1 | 16 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | C2H4Alm |  | stVal |  | OS/SIML1$ST$C2H4Alm$stVal | ✔ | source_1__c2h4__high_high__alarm | 1016
Source 1 C2H4 High Alarm | Source 1 | N/A |  | 1016 | BOOLEAN | N/A |  | 1 | 17 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | C2H4Wrn |  | stVal |  | OS/SIML1$ST$C2H4Wrn$stVal | ✔ | source_1__c2h4__high__alarm | 1017
Source 1 C2H6 High-High Alarm | Source 1 | N/A |  | 1017 | BOOLEAN | N/A |  | 1 | 18 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | C2H6Alm |  | stVal |  | OS/SIML1$ST$C2H6Alm$stVal | ✔ | source_1__c2h6__high_high__alarm | 1018
Source 1 C2H6 High Alarm | Source 1 | N/A |  | 1018 | BOOLEAN | N/A |  | 1 | 19 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | C2H6Wrn |  | stVal |  | OS/SIML1$ST$C2H6Wrn$stVal | ✔ | source_1__c2h6__high__alarm | 1019
Source 1 CH4 High-High Alarm | Source 1 | N/A |  | 1019 | BOOLEAN | N/A |  | 1 | 20 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | CH4Alm |  | stVal |  | OS/SIML1$ST$CH4Alm$stVal | ✔ | source_1__ch4__high_high__alarm | 1020
Source 1 CH4 High Alarm | Source 1 | N/A |  | 1020 | BOOLEAN | N/A |  | 1 | 21 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | CH4Wrn |  | stVal |  | OS/SIML1$ST$CH4Wrn$stVal | ✔ | source_1__ch4__high__alarm | 1021
Source 1 C2H2 High-High Alarm | Source 1 | N/A |  | 1021 | BOOLEAN | N/A |  | 1 | 22 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | C2H2Alm |  | stVal |  | OS/SIML1$ST$C2H2Alm$stVal | ✔ | source_1__c2h2__high_high__alarm | 1022
Source 1 C2H2 High Alarm | Source 1 | N/A |  | 1022 | BOOLEAN | N/A |  | 1 | 23 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | C2H2Wrn |  | stVal |  | OS/SIML1$ST$C2H2Wrn$stVal | ✔ | source_1__c2h2__high__alarm | 1023
Source 1 H2O High-High Alarm | Source 1 | N/A |  | 1023 | BOOLEAN | N/A |  | 1 | 24 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | MstAlm |  | stVal |  | OS/SIML1$ST$MstAlm$stVal | ✔ | source_1__h2o__high_high__alarm | 1024
Source 1 H2O High Alarm | Source 1 | N/A |  | 1024 | BOOLEAN | N/A |  | 1 | 25 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | MstWrn |  | stVal |  | OS/SIML1$ST$MstWrn$stVal | ✔ | source_1__h2o__high__alarm | 1025
Source 1 O2 High-High Alarm | Source 1 | N/A |  | 1025 | BOOLEAN | N/A |  | 1 | 26 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | O2Alm |  | stVal |  | OS/SIML1$ST$O2Alm$stVal | ✔ | source_1__o2__high_high__alarm | 1026
Source 1 O2 High Alarm | Source 1 | N/A |  | 1026 | BOOLEAN | N/A |  | 1 | 27 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | O2Wrn |  | stVal |  | OS/SIML1$ST$O2Wrn$stVal | ✔ | source_1__o2__high__alarm | 1027
Source 1 TDCG High-High Alarm | Source 1 | N/A |  | 1027 | BOOLEAN | N/A |  | 1 | 28 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | CgAlm |  | stVal |  | OS/SIML1$ST$CgAlm$stVal | ✔ | source_1__tdcg__high_high__alarm | 1028
Source 1 TDCG High Alarm | Source 1 | N/A |  | 1028 | BOOLEAN | N/A |  | 1 | 29 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | CgWrn |  | stVal |  | OS/SIML1$ST$CgWrn$stVal | ✔ | source_1__tdcg__high__alarm | 1029
Source 1 N2 High-High Alarm | Source 1 | N/A |  | 1029 | BOOLEAN | N/A |  | 1 | 30 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | N2Alm |  | stVal |  | OS/SIML1$ST$N2Alm$stVal | ✔ | source_1__n2__high_high__alarm | 1030
Source 1 N2 High Alarm | Source 1 | N/A |  | 1030 | BOOLEAN | N/A |  | 1 | 31 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | N2Wrn |  | stVal |  | OS/SIML1$ST$N2Wrn$stVal | ✔ | source_1__n2__high__alarm | 1031
Source 1 H2 ROC High-High Alarm | Source 1 | N/A |  | 1031 | BOOLEAN | N/A |  | 1 | 32 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | H2RteAlm |  | stVal |  | OS/SIML1$ST$H2RteAlm$stVal | ✔ | source_1__h2__roc__high_high__alarm | 1032
Source 1 H2 ROC High Alarm | Source 1 | N/A |  | 1032 | BOOLEAN | N/A |  | 1 | 33 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | H2RteWrn |  | stVal |  | OS/SIML1$ST$H2RteWrn$stVal | ✔ | source_1__h2__roc__high__alarm | 1033
Source 1 CO2 ROC High-High Alarm | Source 1 | N/A |  | 1033 | BOOLEAN | N/A |  | 1 | 34 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | CO2RteAlm |  | stVal |  | OS/SIML1$ST$CO2RteAlm$stVal | ✔ | source_1__co2__roc__high_high__alarm | 1034
Source 1 CO2 ROC High Alarm | Source 1 | N/A |  | 1034 | BOOLEAN | N/A |  | 1 | 35 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | CO2RteWrn |  | stVal |  | OS/SIML1$ST$CO2RteWrn$stVal | ✔ | source_1__co2__roc__high__alarm | 1035
Source 1 CO ROC High-High Alarm | Source 1 | N/A |  | 1035 | BOOLEAN | N/A |  | 1 | 36 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | CORteAlm |  | stVal |  | OS/SIML1$ST$CORteAlm$stVal | ✔ | source_1__co__roc__high_high__alarm | 1036
Source 1 CI ROC High Alarm | Source 1 | N/A |  | 1036 | BOOLEAN | N/A |  | 1 | 37 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | CORteWrn |  | stVal |  | OS/SIML1$ST$CORteWrn$stVal | ✔ | source_1__co__roc__high__alarm | 1037
Source 1 C2H4 ROC High-High Alarm | Source 1 | N/A |  | 1037 | BOOLEAN | N/A |  | 1 | 38 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | C2H4RteAlm |  | stVal |  | OS/SIML1$ST$C2H4RteAlm$stVal | ✔ | source_1__c2h4__roc__high_high__alarm | 1038
Source 1 C2H4 ROC High Alarm | Source 1 | N/A |  | 1038 | BOOLEAN | N/A |  | 1 | 39 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | C2H4RteWrn |  | stVal |  | OS/SIML1$ST$C2H4RteWrn$stVal | ✔ | source_1__c2h4__roc__high__alarm | 1039
Source 1 C2H6 ROC High-High Alarm | Source 1 | N/A |  | 1039 | BOOLEAN | N/A |  | 1 | 40 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | C2H6RteAlm |  | stVal |  | OS/SIML1$ST$C2H6RteAlm$stVal | ✔ | source_1__c2h6__roc__high_high__alarm | 1040
Source 1 C2H6 ROC High Alarm | Source 1 | N/A |  | 1040 | BOOLEAN | N/A |  | 1 | 41 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | C2H6RteWrn |  | stVal |  | OS/SIML1$ST$C2H6RteWrn$stVal | ✔ | source_1__c2h6__roc__high__alarm | 1041
Source 1 CH4 ROC High-High Alarm | Source 1 | N/A |  | 1041 | BOOLEAN | N/A |  | 1 | 42 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | CH4RteAlm |  | stVal |  | OS/SIML1$ST$CH4RteAlm$stVal | ✔ | source_1__ch4__roc__high_high__alarm | 1042
Source 1 CH4 ROC High Alarm | Source 1 | N/A |  | 1042 | BOOLEAN | N/A |  | 1 | 43 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | CH4RteWrn |  | stVal |  | OS/SIML1$ST$CH4RteWrn$stVal | ✔ | source_1__ch4__roc__high__alarm | 1043
Source 1 C2H2 ROC High-High Alarm | Source 1 | N/A |  | 1043 | BOOLEAN | N/A |  | 1 | 44 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | C2H2RteAlm |  | stVal |  | OS/SIML1$ST$C2H2RteAlm$stVal | ✔ | source_1__c2h2__roc__high_high__alarm | 1044
Source 1 C2H2 ROC High Alarm | Source 1 | N/A |  | 1044 | BOOLEAN | N/A |  | 1 | 45 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | C2H2RteWrn |  | stVal |  | OS/SIML1$ST$C2H2RteWrn$stVal | ✔ | source_1__c2h2__roc__high__alarm | 1045
Source 1 H2O ROC High-High Alarm | Source 1 | N/A |  | 1045 | BOOLEAN | N/A |  | 1 | 46 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | MstRteAlm |  | stVal |  | OS/SIML1$ST$MstRteAlm$stVal | ✔ | source_1__h2o__roc__high_high__alarm | 1046
Source 1 H2O ROC High Alarm | Source 1 | N/A |  | 1046 | BOOLEAN | N/A |  | 1 | 47 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | MstRteWrn |  | stVal |  | OS/SIML1$ST$MstRteWrn$stVal | ✔ | source_1__h2o__roc__high__alarm | 1047
Source 1 O2 ROC High-High Alarm | Source 1 | N/A |  | 1047 | BOOLEAN | N/A |  | 1 | 48 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | O2RteAlm |  | stVal |  | OS/SIML1$ST$O2RteAlm$stVal | ✔ | source_1__o2__roc__high_high__alarm | 1048
Source 1 O2 ROC High Alarm | Source 1 | N/A |  | 1048 | BOOLEAN | N/A |  | 1 | 49 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | O2RteWrn |  | stVal |  | OS/SIML1$ST$O2RteWrn$stVal | ✔ | source_1__o2__roc__high__alarm | 1049
Source 1 TDCG ROC High-High Alarm | Source 1 | N/A |  | 1049 | BOOLEAN | N/A |  | 1 | 50 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | CgRteAlm |  | stVal |  | OS/SIML1$ST$CgRteAlm$stVal | ✔ | source_1__tdcg__roc__high_high__alarm | 1050
Source 1 TDCG ROC High Alarm | Source 1 | N/A |  | 1050 | BOOLEAN | N/A |  | 1 | 51 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | CgRteWrn |  | stVal |  | OS/SIML1$ST$CgRteWrn$stVal | ✔ | source_1__tdcg__roc__high__alarm | 1051
Source 1 N2 ROC High-High Alarm | Source 1 | N/A |  | 1051 | BOOLEAN | N/A |  | 1 | 52 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | N2RteAlm |  | stVal |  | OS/SIML1$ST$N2RteAlm$stVal | ✔ | source_1__n2__roc__high_high__alarm | 1052
Source 1 N2 ROC High Alarm | Source 1 | N/A |  | 1052 | BOOLEAN | N/A |  | 1 | 53 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | N2RteWrn |  | stVal |  | OS/SIML1$ST$N2RteWrn$stVal | ✔ | source_1__n2__roc__high__alarm | 1053
Source 1 RS High-High Alarm | Source 1 | N/A |  | 1053 | BOOLEAN | N/A |  | 1 | 54 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | H2OAlm |  | stVal |  | OS/SIML1$ST$H2OAlm$stVal | ✔ | source_1__relative_saturation__high_high__alarm | 1054
Source 1 RS High Alarm | Source 1 | N/A |  | 1054 | BOOLEAN | N/A |  | 1 | 55 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | H2OWrn |  | stVal |  | OS/SIML1$ST$H2OWrn$stVal | ✔ | source_1__relative_saturation__high__alarm | 1055
Source 1 Ratio 1 High-High Alarm | Source 1 | N/A |  | 1055 | BOOLEAN | N/A |  | 1 | 56 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat1AlmH |  | stVal |  | OS/SIML1$ST$Rat1AlmH$stVal | ✔ | source_1__ratio_1__high_high__alarm | 1056
Source 1 Ratio 1 High Alarm | Source 1 | N/A |  | 1056 | BOOLEAN | N/A |  | 1 | 57 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat1WrnH |  | stVal |  | OS/SIML1$ST$Rat1WrnH$stVal | ✔ | source_1__ratio_1__high__alarm | 1057
Source 1 Ratio 1 Low Alarm | Source 1 | N/A |  | 1057 | BOOLEAN | N/A |  | 1 | 58 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat1WrnL |  | stVal |  | OS/SIML1$ST$Rat1WrnL$stVal | ✔ | source_1__ratio_1__low__alarm | 1058
Source 1 Ratio 1 Low-Low Alarm | Source 1 | N/A |  | 1058 | BOOLEAN | N/A |  | 1 | 59 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat1AlmL |  | stVal |  | OS/SIML1$ST$Rat1AlmL$stVal | ✔ | source_1__ratio_1__low_low__alarm | 1059
Source 1 Ratio 2 High-High Alarm | Source 1 | N/A |  | 1059 | BOOLEAN | N/A |  | 1 | 60 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat2AlmH |  | stVal |  | OS/SIML1$ST$Rat2AlmH$stVal | ✔ | source_1__ratio_2__high_high__alarm | 1060
Source 1 Ratio 2 High Alarm | Source 1 | N/A |  | 1060 | BOOLEAN | N/A |  | 1 | 61 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat2WrnH |  | stVal |  | OS/SIML1$ST$Rat2WrnH$stVal | ✔ | source_1__ratio_2__high__alarm | 1061
Source 1 Ratio 2 Low Alarm | Source 1 | N/A |  | 1061 | BOOLEAN | N/A |  | 1 | 62 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat2WrnL |  | stVal |  | OS/SIML1$ST$Rat2WrnL$stVal | ✔ | source_1__ratio_2__low__alarm | 1062
Source 1 Ratio 2 Low-Low Alarm | Source 1 | N/A |  | 1062 | BOOLEAN | N/A |  | 1 | 63 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat2AlmL |  | stVal |  | OS/SIML1$ST$Rat2AlmL$stVal | ✔ | source_1__ratio_2__low_low__alarm | 1063
Source 1 Ratio 3 High-High Alarm | Source 1 | N/A |  | 1063 | BOOLEAN | N/A |  | 1 | 64 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat3AlmH |  | stVal |  | OS/SIML1$ST$Rat3AlmH$stVal | ✔ | source_1__ratio_3__high_high__alarm | 1064
Source 1 Ratio 3 High Alarm | Source 1 | N/A |  | 1064 | BOOLEAN | N/A |  | 1 | 65 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat3WrnH |  | stVal |  | OS/SIML1$ST$Rat3WrnH$stVal | ✔ | source_1__ratio_3__high__alarm | 1065
Source 1 Ratio 3 Low Alarm | Source 1 | N/A |  | 1065 | BOOLEAN | N/A |  | 1 | 66 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat3WrnL |  | stVal |  | OS/SIML1$ST$Rat3WrnL$stVal | ✔ | source_1__ratio_3__low__alarm | 1066
Source 1 Ratio 3 Low-Low Alarm | Source 1 | N/A |  | 1066 | BOOLEAN | N/A |  | 1 | 67 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat3AlmL |  | stVal |  | OS/SIML1$ST$Rat3AlmL$stVal | ✔ | source_1__ratio_3__low_low__alarm | 1067
Source 1 Ratio 4 High-High Alarm | Source 1 | N/A |  | 1067 | BOOLEAN | N/A |  | 1 | 68 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat4AlmH |  | stVal |  | OS/SIML1$ST$Rat4AlmH$stVal | ✔ | source_1__ratio_4__high_high__alarm | 1068
Source 1 Ratio 4 High Alarm | Source 1 | N/A |  | 1068 | BOOLEAN | N/A |  | 1 | 69 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat4WrnH |  | stVal |  | OS/SIML1$ST$Rat4WrnH$stVal | ✔ | source_1__ratio_4__high__alarm | 1069
Source 1 Ratio 4 Low Alarm | Source 1 | N/A |  | 1069 | BOOLEAN | N/A |  | 1 | 70 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat4WrnL |  | stVal |  | OS/SIML1$ST$Rat4WrnL$stVal | ✔ | source_1__ratio_4__low__alarm | 1070
Source 1 Ratio 4 Low-Low Alarm | Source 1 | N/A |  | 1070 | BOOLEAN | N/A |  | 1 | 71 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat4AlmL |  | stVal |  | OS/SIML1$ST$Rat4AlmL$stVal | ✔ | source_1__ratio_4__low_low__alarm | 1071
Source 1 Ratio 5 High-High Alarm | Source 1 | N/A |  | 1071 | BOOLEAN | N/A |  | 1 | 72 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat5AlmH |  | stVal |  | OS/SIML1$ST$Rat5AlmH$stVal | ✔ | source_1__ratio_5__high_high__alarm | 1072
Source 1 Ratio 5 High Alarm | Source 1 | N/A |  | 1072 | BOOLEAN | N/A |  | 1 | 73 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat5WrnH |  | stVal |  | OS/SIML1$ST$Rat5WrnH$stVal | ✔ | source_1__ratio_5__high__alarm | 1073
Source 1 Ratio 5 Low Alarm | Source 1 | N/A |  | 1073 | BOOLEAN | N/A |  | 1 | 74 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat5WrnL |  | stVal |  | OS/SIML1$ST$Rat5WrnL$stVal | ✔ | source_1__ratio_5__low__alarm | 1074
Source 1 Ratio 5 Low-Low Alarm | Source 1 | N/A |  | 1074 | BOOLEAN | N/A |  | 1 | 75 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat5AlmL |  | stVal |  | OS/SIML1$ST$Rat5AlmL$stVal | ✔ | source_1__ratio_5__low_low__alarm | 1075
Source 1 RCDCM ROC High-High Alarm (Ratio of CO2 and CO Calculated) | Source 1 | N/A |  | 1075 | BOOLEAN | N/A |  | 1 | 76 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | RCDCMAlmH |  | stVal |  | OS/SIML1$ST$RCDCMAlmH$stVal | ✔ | source_1__rcdcm__roc__high_high__alarm | 1076
Source 1 RCDCM ROC High Alarm (Ratio of CO2 and CO Calculated) | Source 1 | N/A |  | 1076 | BOOLEAN | N/A |  | 1 | 77 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | RCDCMWrnH |  | stVal |  | OS/SIML1$ST$RCDCMWrnH$stVal | ✔ | source_1__rcdcm__roc__high__alarm | 1077
Source 1 RCDCM ROC Low Alarm (Ratio of CO2 and CO Calculated) | Source 1 | N/A |  | 1077 | BOOLEAN | N/A |  | 1 | 78 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | RCDCMWrnL |  | stVal |  | OS/SIML1$ST$RCDCMWrnL$stVal | ✔ | source_1__rcdcm__roc__low__alarm | 1078
Source 1 RCDCM ROC Low-Low Alarm (Ratio of CO2 and CO Calculated) | Source 1 | N/A |  | 1078 | BOOLEAN | N/A |  | 1 | 79 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | RCDCMAlmL |  | stVal |  | OS/SIML1$ST$RCDCMAlmL$stVal | ✔ | source_1__rcdcm__roc__low_low__alarm | 1079
Source 1 Ratio 6 High-High Alarm | Source 1 | N/A |  | 1079 | BOOLEAN | N/A |  | 1 | 80 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat6AlmH |  | stVal |  | OS/SIML1$ST$Rat6AlmH$stVal | ✔ | source_1__ratio_6__high_high__alarm | 1080
Source 1 Ratio 6 High Alarm | Source 1 | N/A |  | 1080 | BOOLEAN | N/A |  | 1 | 81 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat6WrnH |  | stVal |  | OS/SIML1$ST$Rat6WrnH$stVal | ✔ | source_1__ratio_6__high__alarm | 1081
Source 1 Ratio 6 Low Alarm | Source 1 | N/A |  | 1081 | BOOLEAN | N/A |  | 1 | 82 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat6WrnL |  | stVal |  | OS/SIML1$ST$Rat6WrnL$stVal | ✔ | source_1__ratio_6__low__alarm | 1082
Source 1 Ratio 6 Low-Low Alarm | Source 1 | N/A |  | 1082 | BOOLEAN | N/A |  | 1 | 83 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat6AlmL |  | stVal |  | OS/SIML1$ST$Rat6AlmL$stVal | ✔ | source_1__ratio_6__low_low__alarm | 1083
Source 1 Ratio 7 High-High Alarm | Source 1 | N/A |  | 1083 | BOOLEAN | N/A |  | 1 | 84 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat7AlmH |  | stVal |  | OS/SIML1$ST$Rat7AlmH$stVal | ✔ | source_1__ratio_7__high_high__alarm | 1084
Source 1 Ratio 7 High Alarm | Source 1 | N/A |  | 1084 | BOOLEAN | N/A |  | 1 | 85 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat7WrnH |  | stVal |  | OS/SIML1$ST$Rat7WrnH$stVal | ✔ | source_1__ratio_7__high__alarm | 1085
Source 1 Ratio 7 Low Alarm | Source 1 | N/A |  | 1085 | BOOLEAN | N/A |  | 1 | 86 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat7WrnL |  | stVal |  | OS/SIML1$ST$Rat7WrnL$stVal | ✔ | source_1__ratio_7__low__alarm | 1086
Source 1 Ratio 7 Low-Low Alarm | Source 1 | N/A |  | 1086 | BOOLEAN | N/A |  | 1 | 87 | 1 | 1 | 2 | ✔ | Active |  | OS | SIML1 | ST | Rat7AlmL |  | stVal |  | OS/SIML1$ST$Rat7AlmL$stVal | ✔ | source_1__ratio_7__low_low__alarm | 1087
Analogue Input 1 High-High Alarm | General | N/A |  | 2999 | BOOLEAN | N/A |  | 1 | 2000 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn1AlmH |  | stVal |  | OS/GGIO1$ST$AnIn1AlmH$stVal | ✔ | ain_1__high_high__alarm | 3000
Analogue Input 1 High Alarm | General | N/A |  | 3000 | BOOLEAN | N/A |  | 1 | 2001 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn1WrnH |  | stVal |  | OS/GGIO1$ST$AnIn1WrnH$stVal | ✔ | ain_1__high__alarm | 3001
Analogue Input 1 Low Alarm | General | N/A |  | 3001 | BOOLEAN | N/A |  | 1 | 2002 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn1WrnL |  | stVal |  | OS/GGIO1$ST$AnIn1WrnL$stVal | ✔ | ain_1__low__alarm | 3002
Analogue Input 1 Low-Low Alarm | General | N/A |  | 3002 | BOOLEAN | N/A |  | 1 | 2003 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn1AlmL |  | stVal |  | OS/GGIO1$ST$AnIn1AlmL$stVal | ✔ | ain_1__low_low__alarm | 3003
Analogue Input 2 High-High Alarm | General | N/A |  | 3003 | BOOLEAN | N/A |  | 1 | 2004 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn2AlmH |  | stVal |  | OS/GGIO1$ST$AnIn2AlmH$stVal | ✔ | ain_2__high_high__alarm | 3004
Analogue Input 2 High Alarm | General | N/A |  | 3004 | BOOLEAN | N/A |  | 1 | 2005 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn2WrnH |  | stVal |  | OS/GGIO1$ST$AnIn2WrnH$stVal | ✔ | ain_2__high__alarm | 3005
Analogue Input 2 Low Alarm | General | N/A |  | 3005 | BOOLEAN | N/A |  | 1 | 2006 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn2WrnL |  | stVal |  | OS/GGIO1$ST$AnIn2WrnL$stVal | ✔ | ain_2__low__alarm | 3006
Analogue Input 2 Low-Low Alarm | General | N/A |  | 3006 | BOOLEAN | N/A |  | 1 | 2007 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn2AlmL |  | stVal |  | OS/GGIO1$ST$AnIn2AlmL$stVal | ✔ | ain_2__low_low__alarm | 3007
Analogue Input 3 High-High Alarm | General | N/A |  | 3007 | BOOLEAN | N/A |  | 1 | 2008 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn3AlmH |  | stVal |  | OS/GGIO1$ST$AnIn3AlmH$stVal | ✔ | ain_3__high_high__alarm | 3008
Analogue Input 3 High Alarm | General | N/A |  | 3008 | BOOLEAN | N/A |  | 1 | 2009 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn3WrnH |  | stVal |  | OS/GGIO1$ST$AnIn3WrnH$stVal | ✔ | ain_3__high__alarm | 3009
Analogue Input 3 Low Alarm | General | N/A |  | 3009 | BOOLEAN | N/A |  | 1 | 2010 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn3WrnL |  | stVal |  | OS/GGIO1$ST$AnIn3WrnL$stVal | ✔ | ain_3__low__alarm | 3010
Analogue Input 3 Low-Low Alarm | General | N/A |  | 3010 | BOOLEAN | N/A |  | 1 | 2011 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn3AlmL |  | stVal |  | OS/GGIO1$ST$AnIn3AlmL$stVal | ✔ | ain_3__low_low__alarm | 3011
Analogue Input 4 High-High Alarm | General | N/A |  | 3011 | BOOLEAN | N/A |  | 1 | 2012 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn4AlmH |  | stVal |  | OS/GGIO1$ST$AnIn4AlmH$stVal | ✔ | ain_4__high_high__alarm | 3012
Analogue Input 4 High Alarm | General | N/A |  | 3012 | BOOLEAN | N/A |  | 1 | 2013 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn4WrnH |  | stVal |  | OS/GGIO1$ST$AnIn4WrnH$stVal | ✔ | ain_4__high__alarm | 3013
Analogue Input 4 Low Alarm | General | N/A |  | 3013 | BOOLEAN | N/A |  | 1 | 2014 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn4WrnL |  | stVal |  | OS/GGIO1$ST$AnIn4WrnL$stVal | ✔ | ain_4__low__alarm | 3014
Analogue Input 4 Low-Low Alarm | General | N/A |  | 3014 | BOOLEAN | N/A |  | 1 | 2015 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn4AlmL |  | stVal |  | OS/GGIO1$ST$AnIn4AlmL$stVal | ✔ | ain_4__low_low__alarm | 3015
Analogue Input 5 High-High Alarm | General | N/A |  | 3015 | BOOLEAN | N/A |  | 1 | 2016 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn5AlmH |  | stVal |  | OS/GGIO1$ST$AnIn5AlmH$stVal | ✔ | ain_5__high_high__alarm | 3016
Analogue Input 5 High Alarm | General | N/A |  | 3016 | BOOLEAN | N/A |  | 1 | 2017 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn5WrnH |  | stVal |  | OS/GGIO1$ST$AnIn5WrnH$stVal | ✔ | ain_5__high__alarm | 3017
Analogue Input 5 Low Alarm | General | N/A |  | 3017 | BOOLEAN | N/A |  | 1 | 2018 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn5WrnL |  | stVal |  | OS/GGIO1$ST$AnIn5WrnL$stVal | ✔ | ain_5__low__alarm | 3018
Analogue Input 5 Low-Low Alarm | General | N/A |  | 3018 | BOOLEAN | N/A |  | 1 | 2019 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn5AlmL |  | stVal |  | OS/GGIO1$ST$AnIn5AlmL$stVal | ✔ | ain_5__low_low__alarm | 3019
Analogue Input 6 High-High Alarm | General | N/A |  | 3019 | BOOLEAN | N/A |  | 1 | 2020 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn6AlmH |  | stVal |  | OS/GGIO1$ST$AnIn6AlmH$stVal | ✔ | ain_6__high_high__alarm | 3020
Analogue Input 6 High Alarm | General | N/A |  | 3020 | BOOLEAN | N/A |  | 1 | 2021 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn6WrnH |  | stVal |  | OS/GGIO1$ST$AnIn6WrnH$stVal | ✔ | ain_6__high__alarm | 3021
Analogue Input 6 Low Alarm | General | N/A |  | 3021 | BOOLEAN | N/A |  | 1 | 2022 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn6WrnL |  | stVal |  | OS/GGIO1$ST$AnIn6WrnL$stVal | ✔ | ain_6__low__alarm | 3022
Analogue Input 6 Low-Low Alarm | General | N/A |  | 3022 | BOOLEAN | N/A |  | 1 | 2023 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn6AlmL |  | stVal |  | OS/GGIO1$ST$AnIn6AlmL$stVal | ✔ | ain_6__low_low__alarm | 3023
Digital Input 1 Transition Total High-High Alarm | General | N/A |  | 3023 | BOOLEAN | N/A |  | 1 | 2024 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr1AlmH |  | stVal |  | OS/GGIO1$ST$DiTr1AlmH$stVal | ✔ | din_1__transition_total__high_high__alarm | 3024
Digital Input 1 Transition Total High Alarm | General | N/A |  | 3024 | BOOLEAN | N/A |  | 1 | 2025 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr1WrnH |  | stVal |  | OS/GGIO1$ST$DiTr1WrnH$stVal | ✔ | din_1__transition_total__high__alarm | 3025
Digital Input 2 Transition Total High-High Alarm | General | N/A |  | 3025 | BOOLEAN | N/A |  | 1 | 2026 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr2AlmH |  | stVal |  | OS/GGIO1$ST$DiTr2AlmH$stVal | ✔ | din_2__transition_total__high_high__alarm | 3026
Digital Input 2 Transition Total High Alarm | General | N/A |  | 3026 | BOOLEAN | N/A |  | 1 | 2027 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr2WrnH |  | stVal |  | OS/GGIO1$ST$DiTr2WrnH$stVal | ✔ | din_2__transition_total__high__alarm | 3027
Digital Input 3 Transition Total High-High Alarm | General | N/A |  | 3027 | BOOLEAN | N/A |  | 1 | 2028 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr3AlmH |  | stVal |  | OS/GGIO1$ST$DiTr3AlmH$stVal | ✔ | din_3__transition_total__high_high__alarm | 3028
Digital Input 3 Transition Total High Alarm | General | N/A |  | 3028 | BOOLEAN | N/A |  | 1 | 2029 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr3WrnH |  | stVal |  | OS/GGIO1$ST$DiTr3WrnH$stVal | ✔ | din_3__transition_total__high__alarm | 3029
Digital Input 1 Alarm | General | N/A |  | 3029 | BOOLEAN | N/A |  | 1 | 2030 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | DiIn1Alm |  | stVal |  | OS/GGIO1$ST$DiIn1Alm$stVal | ✔ | din_1__alarm | 3030
Digital Input 2 Alarm | General | N/A |  | 3030 | BOOLEAN | N/A |  | 1 | 2031 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | DiIn2Alm |  | stVal |  | OS/GGIO1$ST$DiIn2Alm$stVal | ✔ | din_2__alarm | 3031
Digital Input 3 Alarm | General | N/A |  | 3031 | BOOLEAN | N/A |  | 1 | 2032 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | DiIn3Alm |  | stVal |  | OS/GGIO1$ST$DiIn3Alm$stVal | ✔ | din_3__alarm | 3032
Digital Input 4 Transition Total High-High Alarm | General | N/A |  | 3032 | BOOLEAN | N/A |  | 1 | 2033 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr4AlmH |  | stVal |  | OS/GGIO1$ST$DiTr4AlmH$stVal | ✔ | din_4__transition_total__high_high__alarm | 3033
Digital Input 4 Transition Total High Alarm | General | N/A |  | 3033 | BOOLEAN | N/A |  | 1 | 2034 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr4WrnH |  | stVal |  | OS/GGIO1$ST$DiTr4WrnH$stVal | ✔ | din_4__transition_total__high__alarm | 3034
Digital Input 5 Transition Total High-High Alarm | General | N/A |  | 3034 | BOOLEAN | N/A |  | 1 | 2035 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr5AlmH |  | stVal |  | OS/GGIO1$ST$DiTr5AlmH$stVal | ✔ | din_5__transition_total__high_high__alarm | 3035
Digital Input 5 Transition Total High Alarm | General | N/A |  | 3035 | BOOLEAN | N/A |  | 1 | 2036 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr5WrnH |  | stVal |  | OS/GGIO1$ST$DiTr5WrnH$stVal | ✔ | din_5__transition_total__high__alarm | 3036
Digital Input 6 Transition Total High-High Alarm | General | N/A |  | 3036 | BOOLEAN | N/A |  | 1 | 2037 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr6AlmH |  | stVal |  | OS/GGIO1$ST$DiTr6AlmH$stVal | ✔ | din_6__transition_total__high_high__alarm | 3037
Digital Input 6 Transition Total High Alarm | General | N/A |  | 3037 | BOOLEAN | N/A |  | 1 | 2038 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr6WrnH |  | stVal |  | OS/GGIO1$ST$DiTr6WrnH$stVal | ✔ | din_6__transition_total__high__alarm | 3038
Digital Input 7 Transition Total High-High Alarm | General | N/A |  | 3038 | BOOLEAN | N/A |  | 1 | 2039 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr7AlmH |  | stVal |  | OS/GGIO1$ST$DiTr7AlmH$stVal | ✔ | din_7__transition_total__high_high__alarm | 3039
Digital Input 7 Transition Total High Alarm | General | N/A |  | 3039 | BOOLEAN | N/A |  | 1 | 2040 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr7WrnH |  | stVal |  | OS/GGIO1$ST$DiTr7WrnH$stVal | ✔ | din_7__transition_total__high__alarm | 3040
Digital Input 8 Transition Total High-High Alarm | General | N/A |  | 3040 | BOOLEAN | N/A |  | 1 | 2041 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr8AlmH |  | stVal |  | OS/GGIO1$ST$DiTr8AlmH$stVal | ✔ | din_8__transition_total__high_high__alarm | 3041
Digital Input 8 Transition Total High Alarm | General | N/A |  | 3041 | BOOLEAN | N/A |  | 1 | 2042 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr8WrnH |  | stVal |  | OS/GGIO1$ST$DiTr8WrnH$stVal | ✔ | din_8__transition_total__high__alarm | 3042
Digital Input 9 Transition Total High-High Alarm | General | N/A |  | 3042 | BOOLEAN | N/A |  | 1 | 2043 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr9AlmH |  | stVal |  | OS/GGIO1$ST$DiTr9AlmH$stVal | ✔ | din_9__transition_total__high_high__alarm | 3043
Digital Input 9 Transition Total High Alarm | General | N/A |  | 3043 | BOOLEAN | N/A |  | 1 | 2044 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiTr9WrnH |  | stVal |  | OS/GGIO1$ST$DiTr9WrnH$stVal | ✔ | din_9__transition_total__high__alarm | 3044
Digital Input 4 Alarm | General | N/A |  | 3044 | BOOLEAN | N/A |  | 1 | 2045 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | DiIn4Alm |  | stVal |  | OS/GGIO1$ST$DiIn4Alm$stVal | ✔ | din_4__alarm | 3045
Digital Input 5 Alarm | General | N/A |  | 3045 | BOOLEAN | N/A |  | 1 | 2046 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | DiIn5Alm |  | stVal |  | OS/GGIO1$ST$DiIn5Alm$stVal | ✔ | din_5__alarm | 3046
Digital Input 6 Alarm | General | N/A |  | 3046 | BOOLEAN | N/A |  | 1 | 2047 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | DiIn6Alm |  | stVal |  | OS/GGIO1$ST$DiIn6Alm$stVal | ✔ | din_6__alarm | 3047
Digital Input 7 Alarm | General | N/A |  | 3047 | BOOLEAN | N/A |  | 1 | 2048 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | DiIn7Alm |  | stVal |  | OS/GGIO1$ST$DiIn7Alm$stVal | ✔ | din_7__alarm | 3048
Digital Input 8 Alarm | General | N/A |  | 3048 | BOOLEAN | N/A |  | 1 | 2049 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | DiIn8Alm |  | stVal |  | OS/GGIO1$ST$DiIn8Alm$stVal | ✔ | din_8__alarm | 3049
Digital Input 9 Alarm | General | N/A |  | 3049 | BOOLEAN | N/A |  | 1 | 2050 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | DiIn9Alm |  | stVal |  | OS/GGIO1$ST$DiIn9Alm$stVal | ✔ | din_9__alarm | 3050
Analogue Input 7 High-High Alarm | General | N/A |  | 3099 | BOOLEAN | N/A |  | 1 | 2100 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn7AlmH |  | stVal |  | OS/GGIO1$ST$AnIn7AlmH$stVal | ✔ | ain_7__high_high__alarm | 3100
Analogue Input 7 High Alarm | General | N/A |  | 3100 | BOOLEAN | N/A |  | 1 | 2101 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn7WrnH |  | stVal |  | OS/GGIO1$ST$AnIn7WrnH$stVal | ✔ | ain_7__high__alarm | 3101
Analogue Input 7 Low Alarm | General | N/A |  | 3101 | BOOLEAN | N/A |  | 1 | 2102 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn7WrnL |  | stVal |  | OS/GGIO1$ST$AnIn7WrnL$stVal | ✔ | ain_7__low__alarm | 3102
Analogue Input 7 Low-Low Alarm | General | N/A |  | 3102 | BOOLEAN | N/A |  | 1 | 2103 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn7AlmL |  | stVal |  | OS/GGIO1$ST$AnIn7AlmL$stVal | ✔ | ain_7__low_low__alarm | 3103
Analogue Input 8 High-High Alarm | General | N/A |  | 3103 | BOOLEAN | N/A |  | 1 | 2104 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn8AlmH |  | stVal |  | OS/GGIO1$ST$AnIn8AlmH$stVal | ✔ | ain_8__high_high__alarm | 3104
Analogue Input 8 High Alarm | General | N/A |  | 3104 | BOOLEAN | N/A |  | 1 | 2105 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn8WrnH |  | stVal |  | OS/GGIO1$ST$AnIn8WrnH$stVal | ✔ | ain_8__high__alarm | 3105
Analogue Input 8 Low Alarm | General | N/A |  | 3105 | BOOLEAN | N/A |  | 1 | 2106 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn8WrnL |  | stVal |  | OS/GGIO1$ST$AnIn8WrnL$stVal | ✔ | ain_8__low__alarm | 3106
Analogue Input 8 Low-Low Alarm | General | N/A |  | 3106 | BOOLEAN | N/A |  | 1 | 2107 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn8AlmL |  | stVal |  | OS/GGIO1$ST$AnIn8AlmL$stVal | ✔ | ain_8__low_low__alarm | 3107
Analogue Input 9 High-High Alarm | General | N/A |  | 3107 | BOOLEAN | N/A |  | 1 | 2108 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn9AlmH |  | stVal |  | OS/GGIO1$ST$AnIn9AlmH$stVal | ✔ | ain_9__high_high__alarm | 3108
Analogue Input 9 High Alarm | General | N/A |  | 3108 | BOOLEAN | N/A |  | 1 | 2109 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn9WrnH |  | stVal |  | OS/GGIO1$ST$AnIn9WrnH$stVal | ✔ | ain_9__high__alarm | 3109
Analogue Input 9 Low Alarm | General | N/A |  | 3109 | BOOLEAN | N/A |  | 1 | 2110 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn9WrnL |  | stVal |  | OS/GGIO1$ST$AnIn9WrnL$stVal | ✔ | ain_9__low__alarm | 3110
Analogue Input 9 Low-Low Alarm | General | N/A |  | 3110 | BOOLEAN | N/A |  | 1 | 2111 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn9AlmL |  | stVal |  | OS/GGIO1$ST$AnIn9AlmL$stVal | ✔ | ain_9__low_low__alarm | 3111
Analogue Input 10 High-High Alarm | General | N/A |  | 3111 | BOOLEAN | N/A |  | 1 | 2112 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn10AlmH |  | stVal |  | OS/GGIO1$ST$AnIn10AlmH$stVal | ✔ | ain_10__high_high__alarm | 3112
Analogue Input 10 High Alarm | General | N/A |  | 3112 | BOOLEAN | N/A |  | 1 | 2113 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn10WrnH |  | stVal |  | OS/GGIO1$ST$AnIn10WrnH$stVal | ✔ | ain_10__high__alarm | 3113
Analogue Input 10 Low Alarm | General | N/A |  | 3113 | BOOLEAN | N/A |  | 1 | 2114 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn10WrnL |  | stVal |  | OS/GGIO1$ST$AnIn10WrnL$stVal | ✔ | ain_10__low__alarm | 3114
Analogue Input 10 Low-Low Alarm | General | N/A |  | 3114 | BOOLEAN | N/A |  | 1 | 2115 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn10AlmL |  | stVal |  | OS/GGIO1$ST$AnIn10AlmL$stVal | ✔ | ain_10__low_low__alarm | 3115
Analogue Input 11 High-High Alarm | General | N/A |  | 3115 | BOOLEAN | N/A |  | 1 | 2116 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn11AlmH |  | stVal |  | OS/GGIO1$ST$AnIn11AlmH$stVal | ✔ | ain_11__high_high__alarm | 3116
Analogue Input 11 High Alarm | General | N/A |  | 3116 | BOOLEAN | N/A |  | 1 | 2117 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn11WrnH |  | stVal |  | OS/GGIO1$ST$AnIn11WrnH$stVal | ✔ | ain_11__high__alarm | 3117
Analogue Input 11 Low Alarm | General | N/A |  | 3117 | BOOLEAN | N/A |  | 1 | 2118 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn11WrnL |  | stVal |  | OS/GGIO1$ST$AnIn11WrnL$stVal | ✔ | ain_11__low__alarm | 3118
Analogue Input 11 Low-Low Alarm | General | N/A |  | 3118 | BOOLEAN | N/A |  | 1 | 2119 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn11AlmL |  | stVal |  | OS/GGIO1$ST$AnIn11AlmL$stVal | ✔ | ain_11__low_low__alarm | 3119
Analogue Input 12 High-High Alarm | General | N/A |  | 3119 | BOOLEAN | N/A |  | 1 | 2120 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn12AlmH |  | stVal |  | OS/GGIO1$ST$AnIn12AlmH$stVal | ✔ | ain_12__high_high__alarm | 3120
Analogue Input 12 High Alarm | General | N/A |  | 3120 | BOOLEAN | N/A |  | 1 | 2121 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn12WrnH |  | stVal |  | OS/GGIO1$ST$AnIn12WrnH$stVal | ✔ | ain_12__high__alarm | 3121
Analogue Input 12 Low Alarm | General | N/A |  | 3121 | BOOLEAN | N/A |  | 1 | 2122 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn12WrnL |  | stVal |  | OS/GGIO1$ST$AnIn12WrnL$stVal | ✔ | ain_12__low__alarm | 3122
Analogue Input 12 Low-Low Alarm | General | N/A |  | 3122 | BOOLEAN | N/A |  | 1 | 2123 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn12AlmL |  | stVal |  | OS/GGIO1$ST$AnIn12AlmL$stVal | ✔ | ain_12__low_low__alarm | 3123
Analogue Input 13 High-High Alarm | General | N/A |  | 3123 | BOOLEAN | N/A |  | 1 | 2124 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn13AlmH |  | stVal |  | OS/GGIO1$ST$AnIn13AlmH$stVal | ✔ | ain_13__high_high__alarm | 3124
Analogue Input 13 High Alarm | General | N/A |  | 3124 | BOOLEAN | N/A |  | 1 | 2125 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn13WrnH |  | stVal |  | OS/GGIO1$ST$AnIn13WrnH$stVal | ✔ | ain_13__high__alarm | 3125
Analogue Input 13 Low Alarm | General | N/A |  | 3125 | BOOLEAN | N/A |  | 1 | 2126 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn13WrnL |  | stVal |  | OS/GGIO1$ST$AnIn13WrnL$stVal | ✔ | ain_13__low__alarm | 3126
Analogue Input 13 Low-Low Alarm | General | N/A |  | 3126 | BOOLEAN | N/A |  | 1 | 2127 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn13AlmL |  | stVal |  | OS/GGIO1$ST$AnIn13AlmL$stVal | ✔ | ain_13__low_low__alarm | 3127
Analogue Input 14 High-High Alarm | General | N/A |  | 3127 | BOOLEAN | N/A |  | 1 | 2128 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn14AlmH |  | stVal |  | OS/GGIO1$ST$AnIn14AlmH$stVal | ✔ | ain_14__high_high__alarm | 3128
Analogue Input 14 High Alarm | General | N/A |  | 3128 | BOOLEAN | N/A |  | 1 | 2129 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn14WrnH |  | stVal |  | OS/GGIO1$ST$AnIn14WrnH$stVal | ✔ | ain_14__high__alarm | 3129
Analogue Input 14 Low Alarm | General | N/A |  | 3129 | BOOLEAN | N/A |  | 1 | 2130 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn14WrnL |  | stVal |  | OS/GGIO1$ST$AnIn14WrnL$stVal | ✔ | ain_14__low__alarm | 3130
Analogue Input 14 Low-Low Alarm | General | N/A |  | 3130 | BOOLEAN | N/A |  | 1 | 2131 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn14AlmL |  | stVal |  | OS/GGIO1$ST$AnIn14AlmL$stVal | ✔ | ain_14__low_low__alarm | 3131
Analogue Input 15 High-High Alarm | General | N/A |  | 3131 | BOOLEAN | N/A |  | 1 | 2132 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn15AlmH |  | stVal |  | OS/GGIO1$ST$AnIn15AlmH$stVal | ✔ | ain_15__high_high__alarm | 3132
Analogue Input 15 High Alarm | General | N/A |  | 3132 | BOOLEAN | N/A |  | 1 | 2133 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn15WrnH |  | stVal |  | OS/GGIO1$ST$AnIn15WrnH$stVal | ✔ | ain_15__high__alarm | 3133
Analogue Input 15 Low Alarm | General | N/A |  | 3133 | BOOLEAN | N/A |  | 1 | 2134 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn15WrnL |  | stVal |  | OS/GGIO1$ST$AnIn15WrnL$stVal | ✔ | ain_15__low__alarm | 3134
Analogue Input 15 Low-Low Alarm | General | N/A |  | 3134 | BOOLEAN | N/A |  | 1 | 2135 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn15AlmL |  | stVal |  | OS/GGIO1$ST$AnIn15AlmL$stVal | ✔ | ain_15__low_low__alarm | 3135
Analogue Input 16 High-High Alarm | General | N/A |  | 3135 | BOOLEAN | N/A |  | 1 | 2136 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn16AlmH |  | stVal |  | OS/GGIO1$ST$AnIn16AlmH$stVal | ✔ | ain_16__high_high__alarm | 3136
Analogue Input 16 High Alarm | General | N/A |  | 3136 | BOOLEAN | N/A |  | 1 | 2137 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn16WrnH |  | stVal |  | OS/GGIO1$ST$AnIn16WrnH$stVal | ✔ | ain_16__high__alarm | 3137
Analogue Input 16 Low Alarm | General | N/A |  | 3137 | BOOLEAN | N/A |  | 1 | 2138 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn16WrnL |  | stVal |  | OS/GGIO1$ST$AnIn16WrnL$stVal | ✔ | ain_16__low__alarm | 3138
Analogue Input 16 Low-Low Alarm | General | N/A |  | 3138 | BOOLEAN | N/A |  | 1 | 2139 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn16AlmL |  | stVal |  | OS/GGIO1$ST$AnIn16AlmL$stVal | ✔ | ain_16__low_low__alarm | 3139
Analogue Input 17 High-High Alarm | General | N/A |  | 3139 | BOOLEAN | N/A |  | 1 | 2140 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn17AlmH |  | stVal |  | OS/GGIO1$ST$AnIn17AlmH$stVal | ✔ | ain_17__high_high__alarm | 3140
Analogue Input 17 High Alarm | General | N/A |  | 3140 | BOOLEAN | N/A |  | 1 | 2141 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn17WrnH |  | stVal |  | OS/GGIO1$ST$AnIn17WrnH$stVal | ✔ | ain_17__high__alarm | 3141
Analogue Input 17 Low Alarm | General | N/A |  | 3141 | BOOLEAN | N/A |  | 1 | 2142 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn17WrnL |  | stVal |  | OS/GGIO1$ST$AnIn17WrnL$stVal | ✔ | ain_17__low__alarm | 3142
Analogue Input 17 Low-Low Alarm | General | N/A |  | 3142 | BOOLEAN | N/A |  | 1 | 2143 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn17AlmL |  | stVal |  | OS/GGIO1$ST$AnIn17AlmL$stVal | ✔ | ain_17__low_low__alarm | 3143
Analogue Input 18 High-High Alarm | General | N/A |  | 3143 | BOOLEAN | N/A |  | 1 | 2144 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn18AlmH |  | stVal |  | OS/GGIO1$ST$AnIn18AlmH$stVal | ✔ | ain_18__high_high__alarm | 3144
Analogue Input 18 High Alarm | General | N/A |  | 3144 | BOOLEAN | N/A |  | 1 | 2145 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn18WrnH |  | stVal |  | OS/GGIO1$ST$AnIn18WrnH$stVal | ✔ | ain_18__high__alarm | 3145
Analogue Input 18 Low Alarm | General | N/A |  | 3145 | BOOLEAN | N/A |  | 1 | 2146 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn18WrnL |  | stVal |  | OS/GGIO1$ST$AnIn18WrnL$stVal | ✔ | ain_18__low__alarm | 3146
Analogue Input 18 Low-Low Alarm | General | N/A |  | 3146 | BOOLEAN | N/A |  | 1 | 2147 | 1 | 1 | 2 | ✔ | Active |  | OS | GGIO1 | ST | AnIn18AlmL |  | stVal |  | OS/GGIO1$ST$AnIn18AlmL$stVal | ✔ | ain_18__low_low__alarm | 3147
TransOpto Channel 1 Temperature High-High Alarm | Trans Opto | N/A |  | 3999 | BOOLEAN | N/A |  | 1 | 3000 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | Tmp1Alm |  | stVal |  | OS/TTMP1$ST$Tmp1Alm$stVal | ✔ | to_temperature_1__high_high__alarm | 4000
TransOpto Channel 1 Temperature High Alarm | Trans Opto | N/A |  | 4000 | BOOLEAN | N/A |  | 1 | 3001 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | Tmp1Wrn |  | stVal |  | OS/TTMP1$ST$Tmp1Wrn$stVal | ✔ | to_temperature_1__high__alarm | 4001
TransOpto Channel 2 Temperature High-High Alarm | Trans Opto | N/A |  | 4001 | BOOLEAN | N/A |  | 1 | 3002 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | Tmp2Alm |  | stVal |  | OS/TTMP1$ST$Tmp2Alm$stVal | ✔ | to_temperature_2__high_high__alarm | 4002
TransOpto Channel 2 Temperature High Alarm | Trans Opto | N/A |  | 4002 | BOOLEAN | N/A |  | 1 | 3003 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | Tmp2Wrn |  | stVal |  | OS/TTMP1$ST$Tmp2Wrn$stVal | ✔ | to_temperature_2__high__alarm | 4003
TransOpto Channel 3 Temperature High-High Alarm | Trans Opto | N/A |  | 4003 | BOOLEAN | N/A |  | 1 | 3004 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | Tmp3Alm |  | stVal |  | OS/TTMP1$ST$Tmp3Alm$stVal | ✔ | to_temperature_3__high_high__alarm | 4004
TransOpto Channel 3 Temperature High Alarm | Trans Opto | N/A |  | 4004 | BOOLEAN | N/A |  | 1 | 3005 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | Tmp3Wrn |  | stVal |  | OS/TTMP1$ST$Tmp3Wrn$stVal | ✔ | to_temperature_3__high__alarm | 4005
TransOpto Channel 4 Temperature High-High Alarm | Trans Opto | N/A |  | 4005 | BOOLEAN | N/A |  | 1 | 3006 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | Tmp4Alm |  | stVal |  | OS/TTMP1$ST$Tmp4Alm$stVal | ✔ | to_temperature_4__high_high__alarm | 4006
TransOpto Channel 4 Temperature High Alarm | Trans Opto | N/A |  | 4006 | BOOLEAN | N/A |  | 1 | 3007 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | Tmp4Wrn |  | stVal |  | OS/TTMP1$ST$Tmp4Wrn$stVal | ✔ | to_temperature_4__high__alarm | 4007
TransOpto Channel 5 Temperature High-High Alarm | Trans Opto | N/A |  | 4007 | BOOLEAN | N/A |  | 1 | 3008 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | Tmp5Alm |  | stVal |  | OS/TTMP1$ST$Tmp5Alm$stVal | ✔ | to_temperature_5__high_high__alarm | 4008
TransOpto Channel 5 Temperature High Alarm | Trans Opto | N/A |  | 4008 | BOOLEAN | N/A |  | 1 | 3009 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | Tmp5Wrn |  | stVal |  | OS/TTMP1$ST$Tmp5Wrn$stVal | ✔ | to_temperature_5__high__alarm | 4009
TransOpto Channel 6 Temperature High-High Alarm | Trans Opto | N/A |  | 4009 | BOOLEAN | N/A |  | 1 | 3010 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | Tmp6Alm |  | stVal |  | OS/TTMP1$ST$Tmp6Alm$stVal | ✔ | to_temperature_6__high_high__alarm | 4010
TransOpto Channel 6 Temperature High Alarm | Trans Opto | N/A |  | 4010 | BOOLEAN | N/A |  | 1 | 3011 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | Tmp6Wrn |  | stVal |  | OS/TTMP1$ST$Tmp6Wrn$stVal | ✔ | to_temperature_6__high__alarm | 4011
TransOpto Channel 7 Temperature High-High Alarm | Trans Opto | N/A |  | 4011 | BOOLEAN | N/A |  | 1 | 3012 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | Tmp7Alm |  | stVal |  | OS/TTMP1$ST$Tmp7Alm$stVal | ✔ | to_temperature_7__high_high__alarm | 4012
TransOpto Channel 7 Temperature High Alarm | Trans Opto | N/A |  | 4012 | BOOLEAN | N/A |  | 1 | 3013 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | Tmp7Wrn |  | stVal |  | OS/TTMP1$ST$Tmp7Wrn$stVal | ✔ | to_temperature_7__high__alarm | 4013
TransOpto Channel 8 Temperature High-High Alarm | Trans Opto | N/A |  | 4013 | BOOLEAN | N/A |  | 1 | 3014 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | Tmp8Alm |  | stVal |  | OS/TTMP1$ST$Tmp8Alm$stVal | ✔ | to_temperature_8__high_high__alarm | 4014
TransOpto Channel 8 Temperature High Alarm | Trans Opto | N/A |  | 4014 | BOOLEAN | N/A |  | 1 | 3015 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | Tmp8Wrn |  | stVal |  | OS/TTMP1$ST$Tmp8Wrn$stVal | ✔ | to_temperature_8__high__alarm | 4015
TransOpto Channel 1 Temperature ROC High-High Alarm | Trans Opto | N/A |  | 4999 | BOOLEAN | N/A |  | 1 | 4000 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | TmpRte1Alm |  | stVal |  | OS/TTMP1$ST$TmpRte1Alm$stVal | ✔ | to_temperature_1__roc__high_high__alarm | 5000
TransOpto Channel 1 Temperature ROC High Alarm | Trans Opto | N/A |  | 5000 | BOOLEAN | N/A |  | 1 | 4001 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | TmpRte1Wrn |  | stVal |  | OS/TTMP1$ST$TmpRte1Wrn$stVal | ✔ | to_temperature_1__roc__high__alarm | 5001
TransOpto Channel 2 Temperature ROC High-High Alarm | Trans Opto | N/A |  | 5001 | BOOLEAN | N/A |  | 1 | 4002 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | TmpRte2Alm |  | stVal |  | OS/TTMP1$ST$TmpRte2Alm$stVal | ✔ | to_temperature_2__roc__high_high__alarm | 5002
TransOpto Channel 2 Temperature ROC High Alarm | Trans Opto | N/A |  | 5002 | BOOLEAN | N/A |  | 1 | 4003 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | TmpRte2Wrn |  | stVal |  | OS/TTMP1$ST$TmpRte2Wrn$stVal | ✔ | to_temperature_2__roc__high__alarm | 5003
TransOpto Channel 3 Temperature ROC High-High Alarm | Trans Opto | N/A |  | 5003 | BOOLEAN | N/A |  | 1 | 4004 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | TmpRte3Alm |  | stVal |  | OS/TTMP1$ST$TmpRte3Alm$stVal | ✔ | to_temperature_3__roc__high_high__alarm | 5004
TransOpto Channel 3 Temperature ROC High Alarm | Trans Opto | N/A |  | 5004 | BOOLEAN | N/A |  | 1 | 4005 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | TmpRte3Wrn |  | stVal |  | OS/TTMP1$ST$TmpRte3Wrn$stVal | ✔ | to_temperature_3__roc__high__alarm | 5005
TransOpto Channel 4 Temperature ROC High-High Alarm | Trans Opto | N/A |  | 5005 | BOOLEAN | N/A |  | 1 | 4006 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | TmpRte4Alm |  | stVal |  | OS/TTMP1$ST$TmpRte4Alm$stVal | ✔ | to_temperature_4__roc__high_high__alarm | 5006
TransOpto Channel 4 Temperature ROC High Alarm | Trans Opto | N/A |  | 5006 | BOOLEAN | N/A |  | 1 | 4007 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | TmpRte4Wrn |  | stVal |  | OS/TTMP1$ST$TmpRte4Wrn$stVal | ✔ | to_temperature_4__roc__high__alarm | 5007
TransOpto Channel 5 Temperature ROC High-High Alarm | Trans Opto | N/A |  | 5007 | BOOLEAN | N/A |  | 1 | 4008 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | TmpRte5Alm |  | stVal |  | OS/TTMP1$ST$TmpRte5Alm$stVal | ✔ | to_temperature_5__roc__high_high__alarm | 5008
TransOpto Channel 5 Temperature ROC High Alarm | Trans Opto | N/A |  | 5008 | BOOLEAN | N/A |  | 1 | 4009 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | TmpRte5Wrn |  | stVal |  | OS/TTMP1$ST$TmpRte5Wrn$stVal | ✔ | to_temperature_5__roc__high__alarm | 5009
TransOpto Channel 6 Temperature ROC High-High Alarm | Trans Opto | N/A |  | 5009 | BOOLEAN | N/A |  | 1 | 4010 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | TmpRte6Alm |  | stVal |  | OS/TTMP1$ST$TmpRte6Alm$stVal | ✔ | to_temperature_6__roc__high_high__alarm | 5010
TransOpto Channel 6 Temperature ROC High Alarm | Trans Opto | N/A |  | 5010 | BOOLEAN | N/A |  | 1 | 4011 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | TmpRte6Wrn |  | stVal |  | OS/TTMP1$ST$TmpRte6Wrn$stVal | ✔ | to_temperature_6__roc__high__alarm | 5011
TransOpto Channel 7 Temperature ROC High-High Alarm | Trans Opto | N/A |  | 5011 | BOOLEAN | N/A |  | 1 | 4012 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | TmpRte7Alm |  | stVal |  | OS/TTMP1$ST$TmpRte7Alm$stVal | ✔ | to_temperature_7__roc__high_high__alarm | 5012
TransOpto Channel 7 Temperature ROC High Alarm | Trans Opto | N/A |  | 5012 | BOOLEAN | N/A |  | 1 | 4013 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | TmpRte7Wrn |  | stVal |  | OS/TTMP1$ST$TmpRte7Wrn$stVal | ✔ | to_temperature_7__roc__high__alarm | 5013
TransOpto Channel 8 Temperature ROC High-High Alarm | Trans Opto | N/A |  | 5013 | BOOLEAN | N/A |  | 1 | 4014 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | TmpRte8Alm |  | stVal |  | OS/TTMP1$ST$TmpRte8Alm$stVal | ✔ | to_temperature_8__roc__high_high__alarm | 5014
TransOpto Channel 8 Temperature ROC High Alarm | Trans Opto | N/A |  | 5014 | BOOLEAN | N/A |  | 1 | 4015 | 1 | 1 | 2 | ✔ | Disabled |  | OS | TTMP1 | ST | TmpRte8Wrn |  | stVal |  | OS/TTMP1$ST$TmpRte8Wrn$stVal | ✔ | to_temperature_8__roc__high__alarm | 5015
Digital Input 1 status | General | N/A |  | 5999 | BOOLEAN | N/A |  | 1 | 5000 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiIn1 |  | stVal |  | OS/GGIO1$ST$DiIn1$stVal | ✔ | din_1 | 6000
Digital Input 2 status | General | N/A |  | 6000 | BOOLEAN | N/A |  | 1 | 5001 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiIn2 |  | stVal |  | OS/GGIO1$ST$DiIn2$stVal | ✔ | din_2 | 6001
Digital Input 3 status | General | N/A |  | 6001 | BOOLEAN | N/A |  | 1 | 5002 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiIn3 |  | stVal |  | OS/GGIO1$ST$DiIn3$stVal | ✔ | din_3 | 6002
Digital Input 4 status | General | N/A |  | 6002 | BOOLEAN | N/A |  | 1 | 5003 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiIn4 |  | stVal |  | OS/GGIO1$ST$DiIn4$stVal | ✔ | din_4 | 6003
Digital Input 5 status | General | N/A |  | 6003 | BOOLEAN | N/A |  | 1 | 5004 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiIn5 |  | stVal |  | OS/GGIO1$ST$DiIn5$stVal | ✔ | din_5 | 6004
Digital Input 6 status | General | N/A |  | 6004 | BOOLEAN | N/A |  | 1 | 5005 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiIn6 |  | stVal |  | OS/GGIO1$ST$DiIn6$stVal | ✔ | din_6 | 6005
Digital Input 7 status | General | N/A |  | 6005 | BOOLEAN | N/A |  | 1 | 5006 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiIn7 |  | stVal |  | OS/GGIO1$ST$DiIn7$stVal | ✔ | din_7 | 6006
Digital Input 8 status | General | N/A |  | 6006 | BOOLEAN | N/A |  | 1 | 5007 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiIn8 |  | stVal |  | OS/GGIO1$ST$DiIn8$stVal | ✔ | din_8 | 6007
Digital Input 9 status | General | N/A |  | 6007 | BOOLEAN | N/A |  | 1 | 5008 | 1 | 1 | 2 | ✔ | Disabled |  | OS | GGIO1 | ST | DiIn9 |  | stVal |  | OS/GGIO1$ST$DiIn9$stVal | ✔ | din_9 | 6008
BM Set1 Power Frequency Deviation Warning | BMT | N/A |  | 6999 | BOOLEAN | N/A |  | 1 | 7000 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | FrqWrn |  | stVal |  | BMT/GGIO2$ST$FrqWrn$stVal | ✔ | bd_1_frequency_warning | 7000
BM Channel 1 No Signal Warning | BMT | N/A |  | 7000 | BOOLEAN | N/A |  | 1 | 7001 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | LosSig1 |  | stVal |  | BMT/ZBSH1$ST$LosSig1$stVal | ✔ | bd_1_no_signal_lf_ch1 | 7001
BM Channel 2 No Signal Warning | BMT | N/A |  | 7001 | BOOLEAN | N/A |  | 1 | 7002 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | LosSig2 |  | stVal |  | BMT/ZBSH1$ST$LosSig2$stVal | ✔ | bd_1_no_signal_lf_ch2 | 7002
BM Channel 3 No Signal Warning | BMT | N/A |  | 7002 | BOOLEAN | N/A |  | 1 | 7003 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | LosSig3 |  | stVal |  | BMT/ZBSH1$ST$LosSig3$stVal | ✔ | bd_1_no_signal_lf_ch3 | 7003
BM Channel 4 No Signal Warning | BMT | N/A |  | 7003 | BOOLEAN | N/A |  | 1 | 7004 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | LosSig4 |  | stVal |  | BMT/ZBSH1$ST$LosSig4$stVal | ✔ | bd_1_no_signal_lf_ch4 | 7004
BM Channel 5 No Signal Warning | BMT | N/A |  | 7004 | BOOLEAN | N/A |  | 1 | 7005 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | LosSig5 |  | stVal |  | BMT/ZBSH1$ST$LosSig5$stVal | ✔ | bd_1_no_signal_lf_ch5 | 7005
BM Channel 6 No Signal Warning | BMT | N/A |  | 7005 | BOOLEAN | N/A |  | 1 | 7006 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | LosSig6 |  | stVal |  | BMT/ZBSH1$ST$LosSig6$stVal | ✔ | bd_1_no_signal_lf_ch6 | 7006
BM Channel 1 Low Bushing Current Warning | BMT | N/A |  | 7006 | BOOLEAN | N/A |  | 1 | 7007 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | LowSig1 |  | stVal |  | BMT/ZBSH1$ST$LowSig1$stVal | ✔ | bd_1_low_bushing_current_ch1 | 7007
BM Channel 2 Low Bushing Current Warning | BMT | N/A |  | 7007 | BOOLEAN | N/A |  | 1 | 7008 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | LowSig2 |  | stVal |  | BMT/ZBSH1$ST$LowSig2$stVal | ✔ | bd_1_low_bushing_current_ch2 | 7008
BM Channel 3 Low Bushing Current Warning | BMT | N/A |  | 7008 | BOOLEAN | N/A |  | 1 | 7009 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | LowSig3 |  | stVal |  | BMT/ZBSH1$ST$LowSig3$stVal | ✔ | bd_1_low_bushing_current_ch3 | 7009
BM Channel 4 Low Bushing Current Warning | BMT | N/A |  | 7009 | BOOLEAN | N/A |  | 1 | 7010 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | LowSig4 |  | stVal |  | BMT/ZBSH1$ST$LowSig4$stVal | ✔ | bd_1_low_bushing_current_ch4 | 7010
BM Channel 5 Low Bushing Current Warning | BMT | N/A |  | 7010 | BOOLEAN | N/A |  | 1 | 7011 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | LowSig5 |  | stVal |  | BMT/ZBSH1$ST$LowSig5$stVal | ✔ | bd_1_low_bushing_current_ch5 | 7011
BM Channel 6 Low Bushing Current Warning | BMT | N/A |  | 7011 | BOOLEAN | N/A |  | 1 | 7012 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | LowSig6 |  | stVal |  | BMT/ZBSH1$ST$LowSig6$stVal | ✔ | bd_1_low_bushing_current_ch6 | 7012
BM Channel 1 Bushing Current Saturation Warning | BMT | N/A |  | 7012 | BOOLEAN | N/A |  | 1 | 7013 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | SatSig1 |  | stVal |  | BMT/ZBSH1$ST$SatSig1$stVal | ✔ | bd_1_bushing_current_saturation_ch1 | 7013
BM Channel 2 Bushing Current Saturation Warning | BMT | N/A |  | 7013 | BOOLEAN | N/A |  | 1 | 7014 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | SatSig2 |  | stVal |  | BMT/ZBSH1$ST$SatSig2$stVal | ✔ | bd_1_bushing_current_saturation_ch2 | 7014
BM Channel 3 Bushing Current Saturation Warning | BMT | N/A |  | 7014 | BOOLEAN | N/A |  | 1 | 7015 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | SatSig3 |  | stVal |  | BMT/ZBSH1$ST$SatSig3$stVal | ✔ | bd_1_bushing_current_saturation_ch3 | 7015
BM Channel 4 Bushing Current Saturation Warning | BMT | N/A |  | 7015 | BOOLEAN | N/A |  | 1 | 7016 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | SatSig4 |  | stVal |  | BMT/ZBSH1$ST$SatSig4$stVal | ✔ | bd_1_bushing_current_saturation_ch4 | 7016
BM Channel 5 Bushing Current Saturation Warning | BMT | N/A |  | 7016 | BOOLEAN | N/A |  | 1 | 7017 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | SatSig5 |  | stVal |  | BMT/ZBSH1$ST$SatSig5$stVal | ✔ | bd_1_bushing_current_saturation_ch5 | 7017
BM Channel 6 Bushing Current Saturation Warning | BMT | N/A |  | 7017 | BOOLEAN | N/A |  | 1 | 7018 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | SatSig6 |  | stVal |  | BMT/ZBSH1$ST$SatSig6$stVal | ✔ | bd_1_bushing_current_saturation_ch6 | 7018
PD Channel 1 High Noise Warning | BMT | N/A |  | 7024 | BOOLEAN | N/A |  | 1 | 7025 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | NoiseSig1 |  | stVal |  | BMT/ZBSH1$ST$NoiseSig1$stVal | ✔ | bd_1_high_hf_noise_ch1 | 7025
PD Channel 2 High Noise Warning | BMT | N/A |  | 7025 | BOOLEAN | N/A |  | 1 | 7026 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | NoiseSig2 |  | stVal |  | BMT/ZBSH1$ST$NoiseSig2$stVal | ✔ | bd_1_high_hf_noise_ch2 | 7026
PD Channel 3 High Noise Warning | BMT | N/A |  | 7026 | BOOLEAN | N/A |  | 1 | 7027 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | NoiseSig3 |  | stVal |  | BMT/ZBSH1$ST$NoiseSig3$stVal | ✔ | bd_1_high_hf_noise_ch3 | 7027
BM Ambient Temperature Sensor Failure Warning | BMT | N/A |  | 7036 | BOOLEAN | N/A |  | 1 | 7037 | 1 | 1 | 2 | ✔ | Active |  | BMT | TTMP1 | ST | Tmp5Fail |  | stVal |  | BMT/TTMP1$ST$Tmp5Fail$stVal | ✔ | bd_1_ambient_sensor_failure | 7037
BM Top Oil Temperature sensor 1 failure Warning | BMT | N/A |  | 7037 | BOOLEAN | N/A |  | 1 | 7038 | 1 | 1 | 2 | ✔ | Active |  | BMT | TTMP1 | ST | Tmp1Fail |  | stVal |  | BMT/TTMP1$ST$Tmp1Fail$stVal | ✔ | bd_1_top_oil1_failure | 7038
BM Top Oil Temperature sensor 2 failure Warning | BMT | N/A |  | 7038 | BOOLEAN | N/A |  | 1 | 7039 | 1 | 1 | 2 | ✔ | Active |  | BMT | TTMP1 | ST | Tmp2Fail |  | stVal |  | BMT/TTMP1$ST$Tmp2Fail$stVal | ✔ | bd_1_top_oil2_failure | 7039
BM Top Oil Temperature sensor 3 failure Warning | BMT | N/A |  | 7039 | BOOLEAN | N/A |  | 1 | 7040 | 1 | 1 | 2 | ✔ | Active |  | BMT | TTMP1 | ST | Tmp3Fail |  | stVal |  | BMT/TTMP1$ST$Tmp3Fail$stVal | ✔ | bd_1_top_oil3_failure | 7040
BM Top Oil Temperature sensor 4 failure Warning | BMT | N/A |  | 7040 | BOOLEAN | N/A |  | 1 | 7041 | 1 | 1 | 2 | ✔ | Active |  | BMT | TTMP1 | ST | Tmp4Fail |  | stVal |  | BMT/TTMP1$ST$Tmp4Fail$stVal | ✔ | bd_1_top_oil4_failure | 7041
BM Channel 1 C1 High-High Alarm | BMT | N/A |  | 7049 | BOOLEAN | N/A |  | 1 | 7050 |  |  |  | ✔ | Active |  | BMT | ZBSH1 | ST | React1AlmH |  | stVal |  | BMT/ZBSH1$ST$React1AlmH$stVal | ✔ | bm_1_c1_ch1__high_high__alarm | 7050
BM Channel 1 C1 High Alarm | BMT | N/A |  | 7050 | BOOLEAN | N/A |  | 1 | 7051 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React1WrnH |  | stVal |  | BMT/ZBSH1$ST$React1WrnH$stVal | ✔ | bm_1_c1_ch1__high__alarm | 7051
BM Channel 1 C1 Low Alarm | BMT | N/A |  | 7051 | BOOLEAN | N/A |  | 1 | 7052 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React1WrnL |  | stVal |  | BMT/ZBSH1$ST$React1WrnL$stVal | ✔ | bm_1_c1_ch1__low__alarm | 7052
BM Channel 1 C1 Low-Low Alarm | BMT | N/A |  | 7052 | BOOLEAN | N/A |  | 1 | 7053 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React1AlmL |  | stVal |  | BMT/ZBSH1$ST$React1AlmL$stVal | ✔ | bm_1_c1_ch1__low_low__alarm | 7053
BM Channel 2 C1 High-High Alarm | BMT | N/A |  | 7053 | BOOLEAN | N/A |  | 1 | 7054 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React2AlmH |  | stVal |  | BMT/ZBSH1$ST$React2AlmH$stVal | ✔ | bm_1_c1_ch2__high_high__alarm | 7054
BM Channel 2 C1 High Alarm | BMT | N/A |  | 7054 | BOOLEAN | N/A |  | 1 | 7055 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React2WrnH |  | stVal |  | BMT/ZBSH1$ST$React2WrnH$stVal | ✔ | bm_1_c1_ch2__high__alarm | 7055
BM Channel 2 C1 Low Alarm | BMT | N/A |  | 7055 | BOOLEAN | N/A |  | 1 | 7056 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React2WrnL |  | stVal |  | BMT/ZBSH1$ST$React2WrnL$stVal | ✔ | bm_1_c1_ch2__low__alarm | 7056
BM Channel 2 C1 Low-Low Alarm | BMT | N/A |  | 7056 | BOOLEAN | N/A |  | 1 | 7057 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React2AlmL |  | stVal |  | BMT/ZBSH1$ST$React2AlmL$stVal | ✔ | bm_1_c1_ch2__low_low__alarm | 7057
BM Channel 3 C1 High-High Alarm | BMT | N/A |  | 7057 | BOOLEAN | N/A |  | 1 | 7058 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React3AlmH |  | stVal |  | BMT/ZBSH1$ST$React3AlmH$stVal | ✔ | bm_1_c1_ch3__high_high__alarm | 7058
BM Channel 3 C1 High Alarm | BMT | N/A |  | 7058 | BOOLEAN | N/A |  | 1 | 7059 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React3WrnH |  | stVal |  | BMT/ZBSH1$ST$React3WrnH$stVal | ✔ | bm_1_c1_ch3__high__alarm | 7059
BM Channel 3 C1 Low Alarm | BMT | N/A |  | 7059 | BOOLEAN | N/A |  | 1 | 7060 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React3WrnL |  | stVal |  | BMT/ZBSH1$ST$React3WrnL$stVal | ✔ | bm_1_c1_ch3__low__alarm | 7060
BM Channel 3 C1 Low-Low Alarm | BMT | N/A |  | 7060 | BOOLEAN | N/A |  | 1 | 7061 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React3AlmL |  | stVal |  | BMT/ZBSH1$ST$React3AlmL$stVal | ✔ | bm_1_c1_ch3__low_low__alarm | 7061
BM Channel 4 C1 High-High Alarm | BMT | N/A |  | 7061 | BOOLEAN | N/A |  | 1 | 7062 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React4AlmH |  | stVal |  | BMT/ZBSH1$ST$React4AlmH$stVal | ✔ | bm_1_c1_ch4__high_high__alarm | 7062
BM Channel 4 C1 High Alarm | BMT | N/A |  | 7062 | BOOLEAN | N/A |  | 1 | 7063 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React4WrnH |  | stVal |  | BMT/ZBSH1$ST$React4WrnH$stVal | ✔ | bm_1_c1_ch4__high__alarm | 7063
BM Channel 4 C1 Low Alarm | BMT | N/A |  | 7063 | BOOLEAN | N/A |  | 1 | 7064 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React4WrnL |  | stVal |  | BMT/ZBSH1$ST$React4WrnL$stVal | ✔ | bm_1_c1_ch4__low__alarm | 7064
BM Channel 4 C1 Low-Low Alarm | BMT | N/A |  | 7064 | BOOLEAN | N/A |  | 1 | 7065 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React4AlmL |  | stVal |  | BMT/ZBSH1$ST$React4AlmL$stVal | ✔ | bm_1_c1_ch4__low_low__alarm | 7065
BM Channel 5 C1 High-High Alarm | BMT | N/A |  | 7065 | BOOLEAN | N/A |  | 1 | 7066 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React5AlmH |  | stVal |  | BMT/ZBSH1$ST$React5AlmH$stVal | ✔ | bm_1_c1_ch5__high_high__alarm | 7066
BM Channel 5 C1 High Alarm | BMT | N/A |  | 7066 | BOOLEAN | N/A |  | 1 | 7067 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React5WrnH |  | stVal |  | BMT/ZBSH1$ST$React5WrnH$stVal | ✔ | bm_1_c1_ch5__high__alarm | 7067
BM Channel 5 C1 Low Alarm | BMT | N/A |  | 7067 | BOOLEAN | N/A |  | 1 | 7068 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React5WrnL |  | stVal |  | BMT/ZBSH1$ST$React5WrnL$stVal | ✔ | bm_1_c1_ch5__low__alarm | 7068
BM Channel 5 C1 Low-Low Alarm | BMT | N/A |  | 7068 | BOOLEAN | N/A |  | 1 | 7069 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React5AlmL |  | stVal |  | BMT/ZBSH1$ST$React5AlmL$stVal | ✔ | bm_1_c1_ch5__low_low__alarm | 7069
BM Channel 6 C1 High-High Alarm | BMT | N/A |  | 7069 | BOOLEAN | N/A |  | 1 | 7070 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React6AlmH |  | stVal |  | BMT/ZBSH1$ST$React6AlmH$stVal | ✔ | bm_1_c1_ch6__high_high__alarm | 7070
BM Channel 6 C1 High Alarm | BMT | N/A |  | 7070 | BOOLEAN | N/A |  | 1 | 7071 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React6WrnH |  | stVal |  | BMT/ZBSH1$ST$React6WrnH$stVal | ✔ | bm_1_c1_ch6__high__alarm | 7071
BM Channel 6 C1 Low Alarm | BMT | N/A |  | 7071 | BOOLEAN | N/A |  | 1 | 7072 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React6WrnL |  | stVal |  | BMT/ZBSH1$ST$React6WrnL$stVal | ✔ | bm_1_c1_ch6__low__alarm | 7072
BM Channel 6 C1 Low-Low Alarm | BMT | N/A |  | 7072 | BOOLEAN | N/A |  | 1 | 7073 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH1 | ST | React6AlmL |  | stVal |  | BMT/ZBSH1$ST$React6AlmL$stVal | ✔ | bm_1_c1_ch6__low_low__alarm | 7073
BM Phase Angle Delta Channels 1-2 High-High Alarm | BMT | N/A |  | 7073 | BOOLEAN | N/A |  | 1 | 7074 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | Phd12AlmH |  | stVal |  | BMT/GGIO2$ST$Phd12AlmH$stVal | ✔ | bo_1_delta_angle_ch12__high_high__alarm | 7074
BM Phase Angle Delta Channels 1-2 High Alarm | BMT | N/A |  | 7074 | BOOLEAN | N/A |  | 1 | 7075 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | Phd12WrnH |  | stVal |  | BMT/GGIO2$ST$Phd12WrnH$stVal | ✔ | bo_1_delta_angle_ch12__high__alarm | 7075
BM Phase Angle Delta Channels 1-3 High-High Alarm | BMT | N/A |  | 7075 | BOOLEAN | N/A |  | 1 | 7076 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | Phd13AlmH |  | stVal |  | BMT/GGIO2$ST$Phd13AlmH$stVal | ✔ | bo_1_delta_angle_ch13__high_high__alarm | 7076
BM Phase Angle Delta Channels 1-3 High Alarm | BMT | N/A |  | 7076 | BOOLEAN | N/A |  | 1 | 7077 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | Phd13WrnH |  | stVal |  | BMT/GGIO2$ST$Phd13WrnH$stVal | ✔ | bo_1_delta_angle_ch13__high__alarm | 7077
BM Phase Angle Delta Channels 4-5 High-High Alarm | BMT | N/A |  | 7077 | BOOLEAN | N/A |  | 1 | 7078 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | Phd45AlmH |  | stVal |  | BMT/GGIO2$ST$Phd45AlmH$stVal | ✔ | bo_1_delta_angle_ch45__high_high__alarm | 7078
BM Phase Angle Delta Channels 4-5 High Alarm | BMT | N/A |  | 7078 | BOOLEAN | N/A |  | 1 | 7079 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | Phd45WrnH |  | stVal |  | BMT/GGIO2$ST$Phd45WrnH$stVal | ✔ | bo_1_delta_angle_ch45__high__alarm | 7079
BM Phase Angle Delta Channels 4-6 High-High Alarm | BMT | N/A |  | 7079 | BOOLEAN | N/A |  | 1 | 7080 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | Phd46AlmH |  | stVal |  | BMT/GGIO2$ST$Phd46AlmH$stVal | ✔ | bo_1_delta_angle_ch46__high_high__alarm | 7080
BM Phase Angle Delta Channels 4-6 High Alarm | BMT | N/A |  | 7080 | BOOLEAN | N/A |  | 1 | 7081 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | Phd46WrnH |  | stVal |  | BMT/GGIO2$ST$Phd46WrnH$stVal | ✔ | bo_1_delta_angle_ch46__high__alarm | 7081
PD Channel 1 Maximum Value High-High Alarm | BMT | N/A |  | 7081 | BOOLEAN | N/A |  | 1 | 7082 | 1 | 1 | 2 | ✔ | Active |  | BMT | SPDC1 | ST | PdMax1AlmH |  | stVal |  | BMT/SPDC1$ST$PdMax1AlmH$stVal | ✔ | bm_1_pd_max_ch1__high_high__alarm | 7082
PD Channel 1 Maximum Value High Alarm | BMT | N/A |  | 7082 | BOOLEAN | N/A |  | 1 | 7083 | 1 | 1 | 2 | ✔ | Active |  | BMT | SPDC1 | ST | PdMax1WrnH |  | stVal |  | BMT/SPDC1$ST$PdMax1WrnH$stVal | ✔ | bm_1_pd_max_ch1__high__alarm | 7083
PD Channel 2 Maximum Value High-High Alarm | BMT | N/A |  | 7083 | BOOLEAN | N/A |  | 1 | 7084 | 1 | 1 | 2 | ✔ | Active |  | BMT | SPDC1 | ST | PdMax2AlmH |  | stVal |  | BMT/SPDC1$ST$PdMax2AlmH$stVal | ✔ | bm_1_pd_max_ch2__high_high__alarm | 7084
PD Channel 2 Maximum Value High Alarm | BMT | N/A |  | 7084 | BOOLEAN | N/A |  | 1 | 7085 | 1 | 1 | 2 | ✔ | Active |  | BMT | SPDC1 | ST | PdMax2WrnH |  | stVal |  | BMT/SPDC1$ST$PdMax2WrnH$stVal | ✔ | bm_1_pd_max_ch2__high__alarm | 7085
PD Channel 3 Maximum Value High-High Alarm | BMT | N/A |  | 7085 | BOOLEAN | N/A |  | 1 | 7086 | 1 | 1 | 2 | ✔ | Active |  | BMT | SPDC1 | ST | PdMax3AlmH |  | stVal |  | BMT/SPDC1$ST$PdMax3AlmH$stVal | ✔ | bm_1_pd_max_ch3__high_high__alarm | 7086
PD Channel 3 Maximum Value High Alarm | BMT | N/A |  | 7086 | BOOLEAN | N/A |  | 1 | 7087 | 1 | 1 | 2 | ✔ | Active |  | BMT | SPDC1 | ST | PdMax3WrnH |  | stVal |  | BMT/SPDC1$ST$PdMax3WrnH$stVal | ✔ | bm_1_pd_max_ch3__high__alarm | 7087
BM Set2 Power Frequency Deviation Warning | BMT | N/A |  | 7156 | BOOLEAN | N/A |  | 1 | 7157 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO3 | ST | FrqWrn |  | stVal |  | BMT/GGIO3$ST$FrqWrn$stVal | ✔ | bd_2_frequency_warning | 7157
BM Channel 7 No Signal Warning | BMT | N/A |  | 7157 | BOOLEAN | N/A |  | 1 | 7158 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | LosSig1 |  | stVal |  | BMT/ZBSH2$ST$LosSig1$stVal | ✔ | bd_2_no_signal_lf_ch1 | 7158
BM Channel 8 No Signal Warning | BMT | N/A |  | 7158 | BOOLEAN | N/A |  | 1 | 7159 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | LosSig2 |  | stVal |  | BMT/ZBSH2$ST$LosSig2$stVal | ✔ | bd_2_no_signal_lf_ch2 | 7159
BM Channel 9 No Signal Warning | BMT | N/A |  | 7159 | BOOLEAN | N/A |  | 1 | 7160 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | LosSig3 |  | stVal |  | BMT/ZBSH2$ST$LosSig3$stVal | ✔ | bd_2_no_signal_lf_ch3 | 7160
BM Channel 7 Low Bushing Current Warning | BMT | N/A |  | 7160 | BOOLEAN | N/A |  | 1 | 7161 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | LowSig1 |  | stVal |  | BMT/ZBSH2$ST$LowSig1$stVal | ✔ | bd_2_low_bushing_current_ch1 | 7161
BM Channel 8 Low Bushing Current Warning | BMT | N/A |  | 7161 | BOOLEAN | N/A |  | 1 | 7162 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | LowSig2 |  | stVal |  | BMT/ZBSH2$ST$LowSig2$stVal | ✔ | bd_2_low_bushing_current_ch2 | 7162
BM Channel 9 Low Bushing Current Warning | BMT | N/A |  | 7162 | BOOLEAN | N/A |  | 1 | 7163 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | LowSig3 |  | stVal |  | BMT/ZBSH2$ST$LowSig3$stVal | ✔ | bd_2_low_bushing_current_ch3 | 7163
BM Channel 7 Bushing Current Saturation Warning | BMT | N/A |  | 7163 | BOOLEAN | N/A |  | 1 | 7164 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | SatSig1 |  | stVal |  | BMT/ZBSH2$ST$SatSig1$stVal | ✔ | bd_2_bushing_current_saturation_ch1 | 7164
BM Channel 8 Bushing Current Saturation Warning | BMT | N/A |  | 7164 | BOOLEAN | N/A |  | 1 | 7165 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | SatSig2 |  | stVal |  | BMT/ZBSH2$ST$SatSig2$stVal | ✔ | bd_2_bushing_current_saturation_ch2 | 7165
BM Channel 9 Bushing Current Saturation Warning | BMT | N/A |  | 7165 | BOOLEAN | N/A |  | 1 | 7166 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | SatSig3 |  | stVal |  | BMT/ZBSH2$ST$SatSig3$stVal | ✔ | bd_2_bushing_current_saturation_ch3 | 7166
BM Channel 7 C1 High-High Alarm | BMT | N/A |  | 7185 | BOOLEAN | N/A |  | 1 | 7186 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | React1AlmH |  | stVal |  | BMT/ZBSH2$ST$React1AlmH$stVal | ✔ | bm_2_c1_ch1__high_high__alarm | 7186
BM Channel 7 C1 High Alarm | BMT | N/A |  | 7186 | BOOLEAN | N/A |  | 1 | 7187 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | React1WrnH |  | stVal |  | BMT/ZBSH2$ST$React1WrnH$stVal | ✔ | bm_2_c1_ch1__high__alarm | 7187
BM Channel 7 C1 Low Alarm | BMT | N/A |  | 7187 | BOOLEAN | N/A |  | 1 | 7188 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | React1WrnL |  | stVal |  | BMT/ZBSH2$ST$React1WrnL$stVal | ✔ | bm_2_c1_ch1__low__alarm | 7188
BM Channel 7 C1 Low-Low Alarm | BMT | N/A |  | 7188 | BOOLEAN | N/A |  | 1 | 7189 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | React1AlmL |  | stVal |  | BMT/ZBSH2$ST$React1AlmL$stVal | ✔ | bm_2_c1_ch1__low_low__alarm | 7189
BM Channel 8 C1 High-High Alarm | BMT | N/A |  | 7189 | BOOLEAN | N/A |  | 1 | 7190 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | React2AlmH |  | stVal |  | BMT/ZBSH2$ST$React2AlmH$stVal | ✔ | bm_2_c1_ch2__high_high__alarm | 7190
BM Channel 8 C1 High Alarm | BMT | N/A |  | 7190 | BOOLEAN | N/A |  | 1 | 7191 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | React2WrnH |  | stVal |  | BMT/ZBSH2$ST$React2WrnH$stVal | ✔ | bm_2_c1_ch2__high__alarm | 7191
BM Channel 8 C1 Low Alarm | BMT | N/A |  | 7191 | BOOLEAN | N/A |  | 1 | 7192 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | React2WrnL |  | stVal |  | BMT/ZBSH2$ST$React2WrnL$stVal | ✔ | bm_2_c1_ch2__low__alarm | 7192
BM Channel 8 C1 Low-Low Alarm | BMT | N/A |  | 7192 | BOOLEAN | N/A |  | 1 | 7193 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | React2AlmL |  | stVal |  | BMT/ZBSH2$ST$React2AlmL$stVal | ✔ | bm_2_c1_ch2__low_low__alarm | 7193
BM Channel 9 C1 High-High Alarm | BMT | N/A |  | 7193 | BOOLEAN | N/A |  | 1 | 7194 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | React3AlmH |  | stVal |  | BMT/ZBSH2$ST$React3AlmH$stVal | ✔ | bm_2_c1_ch3__high_high__alarm | 7194
BM Channel 9 C1 High Alarm | BMT | N/A |  | 7194 | BOOLEAN | N/A |  | 1 | 7195 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | React3WrnH |  | stVal |  | BMT/ZBSH2$ST$React3WrnH$stVal | ✔ | bm_2_c1_ch3__high__alarm | 7195
BM Channel 9 C1 Low Alarm | BMT | N/A |  | 7195 | BOOLEAN | N/A |  | 1 | 7196 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | React3WrnL |  | stVal |  | BMT/ZBSH2$ST$React3WrnL$stVal | ✔ | bm_2_c1_ch3__low__alarm | 7196
BM Channel 9 C1 Low-Low Alarm | BMT | N/A |  | 7196 | BOOLEAN | N/A |  | 1 | 7197 | 1 | 1 | 2 | ✔ | Active |  | BMT | ZBSH2 | ST | React3AlmL |  | stVal |  | BMT/ZBSH2$ST$React3AlmL$stVal | ✔ | bm_2_c1_ch3__low_low__alarm | 7197
BM Phase Angle Delta Channels 7-8 High-High Alarm | BMT | N/A |  | 7197 | BOOLEAN | N/A |  | 1 | 7198 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO3 | ST | Phd12AlmH |  | stVal |  | BMT/GGIO3$ST$Phd12AlmH$stVal | ✔ | bo_2_delta_angle_ch12__high_high__alarm | 7198
BM Phase Angle Delta Channels 7-8 High Alarm | BMT | N/A |  | 7198 | BOOLEAN | N/A |  | 1 | 7199 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO3 | ST | Phd12WrnH |  | stVal |  | BMT/GGIO3$ST$Phd12WrnH$stVal | ✔ | bo_2_delta_angle_ch12__high__alarm | 7199
BM Phase Angle Delta Channels 7-9 High-High Alarm | BMT | N/A |  | 7199 | BOOLEAN | N/A |  | 1 | 7200 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO3 | ST | Phd13AlmH |  | stVal |  | BMT/GGIO3$ST$Phd13AlmH$stVal | ✔ | bo_2_delta_angle_ch13__high_high__alarm | 7200
BM Phase Angle Delta Channels 7-9 High Alarm | BMT | N/A |  | 7200 | BOOLEAN | N/A |  | 1 | 7201 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO3 | ST | Phd13WrnH |  | stVal |  | BMT/GGIO3$ST$Phd13WrnH$stVal | ✔ | bo_2_delta_angle_ch13__high__alarm | 7201
BM Set 1 Polar Plot C1% High-High Alarm | BMT | N/A |  | 7201 | BOOLEAN | N/A |  | 1 | 7202 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | ReactPAlmH |  | stVal |  | BMT/GGIO2$ST$ReactPAlmH$stVal | ✔ | bo_1_c1_primary_modulo__high_high__alarm | 7202
BM Set 1 Polar Plot C1% High Alarm | BMT | N/A |  | 7202 | BOOLEAN | N/A |  | 1 | 7203 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | ReactPWrnH |  | stVal |  | BMT/GGIO2$ST$ReactPWrnH$stVal | ✔ | bo_1_c1_primary_modulo__high__alarm | 7203
BM Set 1 Polar Plot PF% High-High Alarm | BMT | N/A |  | 7203 | BOOLEAN | N/A |  | 1 | 7204 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | LosFactPAlmH |  | stVal |  | BMT/GGIO2$ST$LosFactPAlmH$stVal | ✔ | bo_1_pf_primary_modulo__high_high__alarm | 7204
BM Set 1 Polar Plot PF% High Alarm | BMT | N/A |  | 7204 | BOOLEAN | N/A |  | 1 | 7205 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | LosFactPWrnH |  | stVal |  | BMT/GGIO2$ST$LosFactPWrnH$stVal | ✔ | bo_1_pf_primary_modulo__high__alarm | 7205
BM Set 2 Polar Plot C1% High-High Alarm | BMT | N/A |  | 7205 | BOOLEAN | N/A |  | 1 | 7206 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | ReactSAlmH |  | stVal |  | BMT/GGIO2$ST$ReactSAlmH$stVal | ✔ | bo_1_c1_secondary_modulo__high_high__alarm | 7206
BM Set 2 Polar Plot C1% High Alarm | BMT | N/A |  | 7206 | BOOLEAN | N/A |  | 1 | 7207 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | ReactSWrnH |  | stVal |  | BMT/GGIO2$ST$ReactSWrnH$stVal | ✔ | bo_1_c1_secondary_modulo__high__alarm | 7207
BM Set 2 Polar Plot PF% High-High Alarm | BMT | N/A |  | 7207 | BOOLEAN | N/A |  | 1 | 7208 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | LosFactSAlmH |  | stVal |  | BMT/GGIO2$ST$LosFactSAlmH$stVal | ✔ | bo_1_pf_secondary_modulo__high_high__alarm | 7208
BM Set 2 Polar Plot PF% High Alarm | BMT | N/A |  | 7208 | BOOLEAN | N/A |  | 1 | 7209 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | LosFactSWrnH |  | stVal |  | BMT/GGIO2$ST$LosFactSWrnH$stVal | ✔ | bo_1_pf_secondary_modulo__high__alarm | 7209
BM Set 3 Polar Plot C1% High-High Alarm | BMT | N/A |  | 7209 | BOOLEAN | N/A |  | 1 | 7210 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO3 | ST | ReactPAlmH |  | stVal |  | BMT/GGIO3$ST$ReactPAlmH$stVal | ✔ | bo_2_c1_primary_modulo__high_high__alarm | 7210
BM Set 3 Polar Plot C1% High Alarm | BMT | N/A |  | 7210 | BOOLEAN | N/A |  | 1 | 7211 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO3 | ST | ReactPWrnH |  | stVal |  | BMT/GGIO3$ST$ReactPWrnH$stVal | ✔ | bo_2_c1_primary_modulo__high__alarm | 7211
BM Set 3 Polar Plot PF% High-High Alarm | BMT | N/A |  | 7211 | BOOLEAN | N/A |  | 1 | 7212 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO3 | ST | LosFactPAlmH |  | stVal |  | BMT/GGIO3$ST$LosFactPAlmH$stVal | ✔ | bo_2_pf_primary_modulo__high_high__alarm | 7212
BM Set 3 Polar Plot PF% High Alarm | BMT | N/A |  | 7212 | BOOLEAN | N/A |  | 1 | 7213 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO3 | ST | LosFactPWrnH |  | stVal |  | BMT/GGIO3$ST$LosFactPWrnH$stVal | ✔ | bo_2_pf_primary_modulo__high__alarm | 7213
PD Set 1 PDI (Partial Discharge Intensity) Polar Plot High-High Alarm | BMT | N/A |  | 7213 | BOOLEAN | N/A |  | 1 | 7214 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | PdIdxPAlmH |  | stVal |  | BMT/GGIO2$ST$PdIdxPAlmH$stVal | ✔ | bo_1_pdi_primary_modulo__high_high__alarm | 7214
PD Set 1 PDI (Partial Discharge Intensity) Polar Plot High Alarm | BMT | N/A |  | 7214 | BOOLEAN | N/A |  | 1 | 7215 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | PdIdxPWrnH |  | stVal |  | BMT/GGIO2$ST$PdIdxPWrnH$stVal | ✔ | bo_1_pdi_primary_modulo__high__alarm | 7215
PD Set 1 Average Number of Events per Cycle Polar Plot High-High Alarm | BMT | N/A |  | 7215 | BOOLEAN | N/A |  | 1 | 7216 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | PdCntPAlmH |  | stVal |  | BMT/GGIO2$ST$PdCntPAlmH$stVal | ✔ | bo_1_pd_count_primary_modulo__high_high__alarm | 7216
PD Set 1 Average Number of Events per Cycle Polar Plot High Alarm | BMT | N/A |  | 7216 | BOOLEAN | N/A |  | 1 | 7217 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | PdCntPWrnH |  | stVal |  | BMT/GGIO2$ST$PdCntPWrnH$stVal | ✔ | bo_1_pd_count_primary_modulo__high__alarm | 7217
PD Set 1 Average Charge Polar Plot High-High Alarm | BMT | N/A |  | 7217 | BOOLEAN | N/A |  | 1 | 7218 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | PdValPAlmH |  | stVal |  | BMT/GGIO2$ST$PdValPAlmH$stVal | ✔ | bo_1_pd_value_primary_modulo__high_high__alarm | 7218
PD Set 1 Average Charge Polar Plot High Alarm | BMT | N/A |  | 7218 | BOOLEAN | N/A |  | 1 | 7219 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | PdValPWrnH |  | stVal |  | BMT/GGIO2$ST$PdValPWrnH$stVal | ✔ | bo_1_pd_value_primary_modulo__high__alarm | 7219
BM Top Oil Temperature Sensor 1 (°C) High Alarm | BMT | N/A |  | 7219 | BOOLEAN | N/A |  | 1 | 7220 | 1 | 1 | 2 | ✔ | Active |  | BMT | TTMP1 | ST | Tmp1Wrn |  | stVal |  | BMT/TTMP1$ST$Tmp1Wrn$stVal | ✔ | bm_1_top_oil1__high__alarm | 7220
BM Top Oil Temperature Sensor 2 (°C) High Alarm | BMT | N/A |  | 7220 | BOOLEAN | N/A |  | 1 | 7221 | 1 | 1 | 2 | ✔ | Active |  | BMT | TTMP1 | ST | Tmp2Wrn |  | stVal |  | BMT/TTMP1$ST$Tmp2Wrn$stVal | ✔ | bm_1_top_oil2__high__alarm | 7221
BM Top Oil Temperature Sensor 3 (°C) High Alarm | BMT | N/A |  | 7221 | BOOLEAN | N/A |  | 1 | 7222 | 1 | 1 | 2 | ✔ | Active |  | BMT | TTMP1 | ST | Tmp3Wrn |  | stVal |  | BMT/TTMP1$ST$Tmp3Wrn$stVal | ✔ | bm_1_top_oil3__high__alarm | 7222
BM Top Oil Temperature Sensor 4 (°C) High Alarm | BMT | N/A |  | 7222 | BOOLEAN | N/A |  | 1 | 7223 | 1 | 1 | 2 | ✔ | Active |  | BMT | TTMP1 | ST | Tmp4Wrn |  | stVal |  | BMT/TTMP1$ST$Tmp4Wrn$stVal | ✔ | bm_1_top_oil4__high__alarm | 7223
BM low signal threshold alarm | BMT | N/A |  | 7223 | BOOLEAN | N/A |  | 1 | 7224 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | LowBshAlm |  | stVal |  | BMT/GGIO2$ST$LowBshAlm$stVal | ✔ | bd_low_bushing_current__alarm | 7224
BM over/under frequency alarm | BMT | N/A |  | 7224 | BOOLEAN | N/A |  | 1 | 7225 | 1 | 1 | 2 | ✔ | Active |  | BMT | GGIO2 | ST | LowFrqAlm |  | stVal |  | BMT/GGIO2$ST$LowFrqAlm$stVal | ✔ | bd_frequency_warning__alarm | 7225
1 if Hottest Spot Temperature High-High alarm is ON,, otherwise 0 | Models | N/A |  | 7999 | BOOLEAN | N/A |  | 1 | 8000 | 1 | 1 | 2 | ✔ | Active |  | MO | SPTR1 | ST | HPTmpAlm |  | stVal |  | MO/SPTR1$ST$HPTmpAlm$stVal | ✔ | mo_whst_winding_hottest_hot_spot_temperature__high_high__alarm | 8000
1 if Hottest Spot Temperature High alarm is ON,, otherwise 0 | Models | N/A |  | 8000 | BOOLEAN | N/A |  | 1 | 8001 | 1 | 1 | 2 | ✔ | Active |  | MO | SPTR1 | ST | HPTmpWrn |  | stVal |  | MO/SPTR1$ST$HPTmpWrn$stVal | ✔ | mo_whst_winding_hottest_hot_spot_temperature__high__alarm | 8001
1 if Water Condensation Temperature High-High alarm is ON,, otherwise 0 | Models | N/A |  | 8001 | BOOLEAN | N/A |  | 1 | 8002 | 1 | 1 | 2 | ✔ | Active |  | MO | SPTR1 | ST | CdsTmpAlm |  | stVal |  | MO/SPTR1$ST$CdsTmpAlm$stVal | ✔ | mo_mco_water_cond_temp__high_high__alarm | 8002
1 if Water Condensation Temperature High alarm is ON,, otherwise 0 | Models | N/A |  | 8002 | BOOLEAN | N/A |  | 1 | 8003 | 1 | 1 | 2 | ✔ | Active |  | MO | SPTR1 | ST | CdsTmpWrn |  | stVal |  | MO/SPTR1$ST$CdsTmpWrn$stVal | ✔ | mo_mco_water_cond_temp__high__alarm | 8003
1 if Bubbling Temperature Margin Low alarm is ON,, otherwise 0 | Models | N/A |  | 8003 | BOOLEAN | N/A |  | 1 | 8004 | 1 | 1 | 2 | ✔ | Active |  | MO | SPTR1 | ST | BubTmpAlm |  | stVal |  | MO/SPTR1$ST$BubTmpAlm$stVal | ✔ | mo_mstwind_bubbling_temperature_margin__low__alarm | 8004
1 if Bubbling Temperature Margin Low-Low alarm is ON,, otherwise 0 | Models | N/A |  | 8004 | BOOLEAN | N/A |  | 1 | 8005 | 1 | 1 | 2 | ✔ | Active |  | MO | SPTR1 | ST | BubTmpWrn |  | stVal |  | MO/SPTR1$ST$BubTmpWrn$stVal | ✔ | mo_mstwind_bubbling_temperature_margin__low_low__alarm | 8005
1 if Moisture Content in Insulating Barriers High-High alarm is ON,, otherwise 0 | Models | N/A |  | 8005 | BOOLEAN | N/A |  | 1 | 8006 | 1 | 1 | 2 | ✔ | Active |  | MO | SPTR1 | ST | MstAlm |  | stVal |  | MO/SPTR1$ST$MstAlm$stVal | ✔ | mo_mstinsbar_moisture_insulation_barrier__high_high__alarm | 8006
1 if Moisture Content in Insulating Barriers High alarm is ON,, otherwise 0 | Models | N/A |  | 8006 | BOOLEAN | N/A |  | 1 | 8007 | 1 | 1 | 2 | ✔ | Active |  | MO | SPTR1 | ST | MstWrn |  | stVal |  | MO/SPTR1$ST$MstWrn$stVal | ✔ | mo_mstinsbar_moisture_insulation_barrier__high__alarm | 8007
1 if Cooling Bank 1 Deficiency Alarm is ON,, otherwise 0 | Models | N/A |  | 8007 | BOOLEAN | N/A |  | 1 | 8008 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Alm1 |  | stVal |  | MO/GGIO4$ST$Alm1$stVal | ✔ | mo_csm_cooling_bank_1_deficiency_alarm__alarm | 8008
1 if Cooling Bank 2 Deficiency Alarm is ON,, otherwise 0 | Models | N/A |  | 8008 | BOOLEAN | N/A |  | 1 | 8009 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Alm2 |  | stVal |  | MO/GGIO4$ST$Alm2$stVal | ✔ | mo_csm_cooling_bank_2_deficiency_alarm__alarm | 8009
1 if Cooling Bank 3 Deficiency Alarm is ON,, otherwise 0 | Models | N/A |  | 8009 | BOOLEAN | N/A |  | 1 | 8010 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Alm3 |  | stVal |  | MO/GGIO4$ST$Alm3$stVal | ✔ | mo_csm_cooling_bank_3_deficiency_alarm__alarm | 8010
1 if Cooling Bank 4 Deficiency Alarm is ON,, otherwise 0 | Models | N/A |  | 8010 | BOOLEAN | N/A |  | 1 | 8011 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Alm4 |  | stVal |  | MO/GGIO4$ST$Alm4$stVal | ✔ | mo_csm_cooling_bank_4_deficiency_alarm__alarm | 8011
1 if Cooling Bank 1 Overcurrent Warning is ON,, otherwise 0 | Models | N/A |  | 8011 | BOOLEAN | N/A |  | 1 | 8012 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Wrn1 |  | stVal |  | MO/GGIO4$ST$Wrn1$stVal | ✔ | mo_csm_cooling_bank_1_over_current_warning__alarm | 8012
1 if Cooling Bank 2 Overcurrent Warning is ON,, otherwise 0 | Models | N/A |  | 8012 | BOOLEAN | N/A |  | 1 | 8013 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Wrn2 |  | stVal |  | MO/GGIO4$ST$Wrn2$stVal | ✔ | mo_csm_cooling_bank_2_over_current_warning__alarm | 8013
1 if Cooling Bank 3 Overcurrent Warning is ON,, otherwise 0 | Models | N/A |  | 8013 | BOOLEAN | N/A |  | 1 | 8014 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Wrn3 |  | stVal |  | MO/GGIO4$ST$Wrn3$stVal | ✔ | mo_csm_cooling_bank_3_over_current_warning__alarm | 8014
1 if Cooling Bank 4 Overcurrent Warning is ON,, otherwise 0 | Models | N/A |  | 8014 | BOOLEAN | N/A |  | 1 | 8015 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Wrn4 |  | stVal |  | MO/GGIO4$ST$Wrn4$stVal | ✔ | mo_csm_cooling_bank_4_over_current_warning__alarm | 8015
1 if Cooling Bank 1 Overcurrent Alarm is ON,, otherwise 0 | Models | N/A |  | 8015 | BOOLEAN | N/A |  | 1 | 8016 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Alm5 |  | stVal |  | MO/GGIO4$ST$Alm5$stVal | ✔ | mo_csm_cooling_bank_1_over_current_alarm__alarm | 8016
1 if Cooling Bank 2 Overcurrent Alarm is ON,, otherwise 0 | Models | N/A |  | 8016 | BOOLEAN | N/A |  | 1 | 8017 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Alm6 |  | stVal |  | MO/GGIO4$ST$Alm6$stVal | ✔ | mo_csm_cooling_bank_2_over_current_alarm__alarm | 8017
1 if Cooling Bank 3 Overcurrent Alarm is ON,, otherwise 0 | Models | N/A |  | 8017 | BOOLEAN | N/A |  | 1 | 8018 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Alm7 |  | stVal |  | MO/GGIO4$ST$Alm7$stVal | ✔ | mo_csm_cooling_bank_3_over_current_alarm__alarm | 8018
1 if Cooling Bank 4 Overcurrent Alarm is ON,, otherwise 0 | Models | N/A |  | 8018 | BOOLEAN | N/A |  | 1 | 8019 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Alm8 |  | stVal |  | MO/GGIO4$ST$Alm8$stVal | ✔ | mo_csm_cooling_bank_4_over_current_alarm__alarm | 8019
1 if Cooling Stage Malfunction Alarm is ON,, otherwise 0 | Models | N/A |  | 8019 | BOOLEAN | N/A |  | 1 | 8020 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Alm9 |  | stVal |  | MO/GGIO4$ST$Alm9$stVal | ✔ | mo_csm_cooling_stage_malfunction__alarm | 8020
1 if Cooling Bank 1 Continuous Non-Operational Time High-High Alarm is ON,, otherwise 0 | Models | N/A |  | 8020 | BOOLEAN | N/A |  | 1 | 8021 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Alm10 |  | stVal |  | MO/GGIO4$ST$Alm10$stVal | ✔ | mo_csm_cooling_bank_1_continuous_nonoperational_time_hour__high__alarm | 8021
1 if Cooling Bank 2 Continuous Non-Operational Time High-High Alarm is ON,, otherwise 0 | Models | N/A |  | 8021 | BOOLEAN | N/A |  | 1 | 8022 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Alm11 |  | stVal |  | MO/GGIO4$ST$Alm11$stVal | ✔ | mo_csm_cooling_bank_2_continuous_nonoperational_time_hour__high__alarm | 8022
1 if Cooling Bank 3 Continuous Non-Operational Time High-High Alarm is ON,, otherwise 0 | Models | N/A |  | 8022 | BOOLEAN | N/A |  | 1 | 8023 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Alm12 |  | stVal |  | MO/GGIO4$ST$Alm12$stVal | ✔ | mo_csm_cooling_bank_3_continuous_nonoperational_time_hour__high__alarm | 8023
1 if Cooling Bank 4 Continuous Non-Operational Time High-High Alarm is ON,, otherwise 0 | Models | N/A |  | 8023 | BOOLEAN | N/A |  | 1 | 8024 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Alm13 |  | stVal |  | MO/GGIO4$ST$Alm13$stVal | ✔ | mo_csm_cooling_bank_4_continuous_nonoperational_time_hour__high__alarm | 8024
1 if Cooling Efficiency High-High alarm is ON,, otherwise 0 | Models | N/A |  | 8024 | BOOLEAN | N/A |  | 1 | 8025 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Alm14 |  | stVal |  | MO/GGIO4$ST$Alm14$stVal | ✔ | mo_cem_temp_diff_avr__high_high__alarm | 8025
1 if Cooling Efficiency High alarm is ON,, otherwise 0 | Models | N/A |  | 8025 | BOOLEAN | N/A |  | 1 | 8026 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Wrn5 |  | stVal |  | MO/GGIO4$ST$Wrn5$stVal | ✔ | mo_cem_temp_diff_avr__high__alarm | 8026
1 if Short Term Average of OLTC Temperature Differential High-High Alarm is ON,, otherwise 0 | Models | N/A |  | 8026 | BOOLEAN | N/A |  | 1 | 8027 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | Tmp1Alm |  | stVal |  | MO/SLTC1$ST$Tmp1Alm$stVal | ✔ | mo_oltc_temp_oil_short_term_diff__high_high__alarm | 8027
1 if Short Term Average of OLTC Temperature Differential High Alarm is ON,, otherwise 0 | Models | N/A |  | 8027 | BOOLEAN | N/A |  | 1 | 8028 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | Tmp1Wrn |  | stVal |  | MO/SLTC1$ST$Tmp1Wrn$stVal | ✔ | mo_oltc_temp_oil_short_term_diff__high__alarm | 8028
1 if Longt Term Average of OLTC Temperature Differential High-High Alarm is ON,, otherwise 0 | Models | N/A |  | 8028 | BOOLEAN | N/A |  | 1 | 8029 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | Tmp2Alm |  | stVal |  | MO/SLTC1$ST$Tmp2Alm$stVal | ✔ | mo_oltc_temp_oil_long_term_diff__high_high__alarm | 8029
1 if Long Term Average of OLTC Temperature Differential High Alarm is ON,, otherwise 0 | Models | N/A |  | 8029 | BOOLEAN | N/A |  | 1 | 8030 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | Tmp2Wrn |  | stVal |  | MO/SLTC1$ST$Tmp2Wrn$stVal | ✔ | mo_oltc_temp_oil_long_term_diff__high__alarm | 8030
1 if Number of OLTC operations per hour High-High Alarm is ON,, otherwise 0 | Models | N/A |  | 8030 | BOOLEAN | N/A |  | 1 | 8031 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | OpRte1Alm |  | stVal |  | MO/SLTC1$ST$OpRte1Alm$stVal | ✔ | mo_oltc_tp_operations_per_hour__high_high__alarm | 8031
1 if Number of OLTC operations per hour High Alarm is ON,, otherwise 0 | Models | N/A |  | 8031 | BOOLEAN | N/A |  | 1 | 8032 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | OpRte1Wrn |  | stVal |  | MO/SLTC1$ST$OpRte1Wrn$stVal | ✔ | mo_oltc_tp_operations_per_hour__high__alarm | 8032
1 if Number of OLTC operations per day High-High Alarm is ON,, otherwise 0 | Models | N/A |  | 8032 | BOOLEAN | N/A |  | 1 | 8033 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | OpRte2Alm |  | stVal |  | MO/SLTC1$ST$OpRte2Alm$stVal | ✔ | mo_oltc_tp_operations_per_day__high_high__alarm | 8033
1 if Number of OLTC operations per day High Alarm is ON,, otherwise 0 | Models | N/A |  | 8033 | BOOLEAN | N/A |  | 1 | 8034 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | OpRte2Wrn |  | stVal |  | MO/SLTC1$ST$OpRte2Wrn$stVal | ✔ | mo_oltc_tp_operations_per_day__high__alarm | 8034
OLTC Motor Torque Total Time (%).High-High | Models | N/A |  | 8034 | BOOLEAN | N/A |  | 1 | 8035 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | TorqTm1Alm |  | stVal |  | MO/SLTC1$ST$TorqTm1Alm$stVal | ✔ | mo_oltc_torque_total_time_pct__high_high__alarm | 8035
OLTC Motor Torque Total Time (%).High | Models | N/A |  | 8035 | BOOLEAN | N/A |  | 1 | 8036 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | TorqTm1Wrn |  | stVal |  | MO/SLTC1$ST$TorqTm1Wrn$stVal | ✔ | mo_oltc_torque_total_time_pct__high__alarm | 8036
OLTC Motor Torque In-Rush Time(%).High-High | Models | N/A |  | 8036 | BOOLEAN | N/A |  | 1 | 8037 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | TorqTm2Alm |  | stVal |  | MO/SLTC1$ST$TorqTm2Alm$stVal | ✔ | mo_oltc_torque_inrush_time_pct__high_high__alarm | 8037
OLTC Motor Torque In-Rush Time(%).High | Models | N/A |  | 8037 | BOOLEAN | N/A |  | 1 | 8038 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | TorqTm2Wrn |  | stVal |  | MO/SLTC1$ST$TorqTm2Wrn$stVal | ✔ | mo_oltc_torque_inrush_time_pct__high__alarm | 8038
OLTC Motor Torque Maximum 1 (%).High-High | Models | N/A |  | 8038 | BOOLEAN | N/A |  | 1 | 8039 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | Torq1Alm |  | stVal |  | MO/SLTC1$ST$Torq1Alm$stVal | ✔ | mo_oltc_torque_max_pwr1_pct__high_high__alarm | 8039
OLTC Motor Torque Maximum 1 (%). High | Models | N/A |  | 8039 | BOOLEAN | N/A |  | 1 | 8040 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | Torq1Wrn |  | stVal |  | MO/SLTC1$ST$Torq1Wrn$stVal | ✔ | mo_oltc_torque_max_pwr1_pct__high__alarm | 8040
OLTC Motor Torque Maximum 2 (%). High-High | Models | N/A |  | 8040 | BOOLEAN | N/A |  | 1 | 8041 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | Torq2Alm |  | stVal |  | MO/SLTC1$ST$Torq2Alm$stVal | ✔ | mo_oltc_torque_max_pwr2_pct__high_high__alarm | 8041
OLTC Motor Torque Maximum 2 (%). High | Models | N/A |  | 8041 | BOOLEAN | N/A |  | 1 | 8042 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | Torq2Wrn |  | stVal |  | MO/SLTC1$ST$Torq2Wrn$stVal | ✔ | mo_oltc_torque_max_pwr2_pct__high__alarm | 8042
OLTC Motor Torque Maximum 3 (%).High-High | Models | N/A |  | 8042 | BOOLEAN | N/A |  | 1 | 8043 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | Torq3Alm |  | stVal |  | MO/SLTC1$ST$Torq3Alm$stVal | ✔ | mo_oltc_torque_max_pwr3_pct__high_high__alarm | 8043
OLTC Motor Torque Maximum 3 (%).High | Models | N/A |  | 8043 | BOOLEAN | N/A |  | 1 | 8044 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | Torq3Wrn |  | stVal |  | MO/SLTC1$ST$Torq3Wrn$stVal | ✔ | mo_oltc_torque_max_pwr3_pct__high__alarm | 8044
OLTC Motor Average Torque (%).High-High | Models | N/A |  | 8044 | BOOLEAN | N/A |  | 1 | 8045 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | TorqAvgAlm |  | stVal |  | MO/SLTC1$ST$TorqAvgAlm$stVal | ✔ | mo_oltc_torque_avg_pwr_pct__high_high__alarm | 8045
OLTC Motor Average Torque (%).High | Models | N/A |  | 8045 | BOOLEAN | N/A |  | 1 | 8046 | 1 | 1 | 2 | ✔ | Active |  | MO | SLTC1 | ST | TorqAvgWrn |  | stVal |  | MO/SLTC1$ST$TorqAvgWrn$stVal | ✔ | mo_oltc_torque_avg_pwr_pct__high__alarm | 8046
1 if Cooling Bank 1 is ON,, otherwise 0 | Models | N/A |  | 8046 | BOOLEAN | N/A |  | 1 | 8047 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Ind1 |  | stVal |  | MO/GGIO4$ST$Ind1$stVal | ✔ | mo_csm_cooling_bank_1_on | 8047
1 if Cooling Bank 2 is ON,, otherwise 0 | Models | N/A |  | 8047 | BOOLEAN | N/A |  | 1 | 8048 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Ind2 |  | stVal |  | MO/GGIO4$ST$Ind2$stVal | ✔ | mo_csm_cooling_bank_2_on | 8048
1 if Cooling Bank 3 is ON,, otherwise 0 | Models | N/A |  | 8048 | BOOLEAN | N/A |  | 1 | 8049 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Ind3 |  | stVal |  | MO/GGIO4$ST$Ind3$stVal | ✔ | mo_csm_cooling_bank_3_on | 8049
1 if Cooling Bank 4 is ON,, otherwise 0 | Models | N/A |  | 8049 | BOOLEAN | N/A |  | 1 | 8050 | 1 | 1 | 2 | ✔ | Active |  | MO | GGIO4 | ST | Ind4 |  | stVal |  | MO/GGIO4$ST$Ind4$stVal | ✔ | mo_csm_cooling_bank_4_on | 8050
Source 1 H2 conc. (ppm) (Hydrogen) | Source 1 | 5 - 5,000 ppm |  | 999 | FLOAT32 | 1 |  | 30 | 0 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | H2ppm |  | mag | f | OS/SIML1$MX$H2ppm$mag$f | ✔ | source_1__h2 | 1000
Source 1 CO2 conc. (ppm) (Carbon Dioxide) | Source 1 | 20 - 50,000 ppm |  | 1001 | FLOAT32 | 1 |  | 30 | 1 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | CO2ppm |  | mag | f | OS/SIML1$MX$CO2ppm$mag$f | ✔ | source_1__co2 | 1002
Source 1 CO conc. (ppm) (Carbon Monoxide) | Source 1 | 1 - 50,000 ppm |  | 1003 | FLOAT32 | 1 |  | 30 | 2 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | COppm |  | mag | f | OS/SIML1$MX$COppm$mag$f | ✔ | source_1__co | 1004
Source 1 C2H4 conc. (ppm) (Ethylene) | Source 1 | 1 - 50,000 ppm |  | 1005 | FLOAT32 | 1 |  | 30 | 3 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | C2H4ppm |  | mag | f | OS/SIML1$MX$C2H4ppm$mag$f | ✔ | source_1__c2h4 | 1006
Source 1 C2H6 conc. (ppm) (Ethane) | Source 1 | 1 - 50,000 ppm |  | 1007 | FLOAT32 | 1 |  | 30 | 4 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | C2H6ppm |  | mag | f | OS/SIML1$MX$C2H6ppm$mag$f | ✔ | source_1__c2h6 | 1008
Source 1 CH4 conc. (ppm) (Methane) | Source 1 | 2 - 50,000 ppm |  | 1009 | FLOAT32 | 1 |  | 30 | 5 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | CH4ppm |  | mag | f | OS/SIML1$MX$CH4ppm$mag$f | ✔ | source_1__ch4 | 1010
Source 1 C2H2 conc. (ppm) (Acetylene) | Source 1 | 0.5 - 50,000 ppm |  | 1011 | FLOAT32 | 1 |  | 30 | 6 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | C2H2ppm |  | mag | f | OS/SIML1$MX$C2H2ppm$mag$f | ✔ | source_1__c2h2 | 1012
Source 1 H2O conc. (ppm) (Water) | Source 1 | 0 - 10,000 ppm |  | 1013 | FLOAT32 | 1 |  | 30 | 7 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | Mst |  | mag | f | OS/SIML1$MX$Mst$mag$f | ✔ | source_1__h2o | 1014
Source 1 O2 conc. (ppm) (Oxygen) | Source 1 | 100 - 50,000 ppm |  | 1015 | FLOAT32 | 1 |  | 30 | 8 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | O2ppm |  | mag | f | OS/SIML1$MX$O2ppm$mag$f | ✔ | source_1__o2 | 1016
Source 1 TDCG conc. (ppm) (Total Dissolved Combustible Gases) | Source 1 | 0 - 50,000 ppm |  | 1017 | FLOAT32 | 1 |  | 30 | 9 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | CmbuGas |  | mag | f | OS/SIML1$MX$CmbuGas$mag$f | ✔ | source_1__tdcg | 1018
Source 1 N2 conc. (ppm) (Nitrogen) | Source 1 | 10,000 - 50,000 ppm |  | 1019 | FLOAT32 | 1 |  | 30 | 10 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | N2ppm |  | mag | f | OS/SIML1$MX$N2ppm$mag$f | ✔ | source_1__n2 | 1020
Source 1 TDG conc. (ppm) (Total Dissolved Gas) | Source 1 | 0 - 100,000 ppm |  | 1021 | FLOAT32 | 1 |  | 30 | 11 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | FullGas |  | mag | f | OS/SIML1$MX$FullGas$mag$f | ✔ | source_1__tdg | 1022
Source 1 TDH conc. (ppm) (Total Dissolved Hydrocarbons) | Source 1 | 0 - 100,000 ppm |  | 1023 | FLOAT32 | 1 |  | 30 | 12 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | HCGas |  | mag | f | OS/SIML1$MX$HCGas$mag$f | ✔ | source_1__tdh | 1024
Source 1 ESHL (%) (Estimated Safe Handling Limit) | Source 1 | 0 - 100 % |  | 1025 | FLOAT32 | 1 |  | 30 | 13 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | CmbuLim |  | mag | f | OS/SIML1$MX$CmbuLim$mag$f | ✔ | source_1__eshl | 1026
Source 1 Oil Pressure (kPa) | Source 1 | -100 - 500 kPa |  | 1027 | FLOAT32 | 1 |  | 30 | 14 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | Pres |  | mag | f | OS/SIML1$MX$Pres$mag$f | ✔ | source_1__oil_pressure | 1028
Source 1 Oil Temperature (°C) | Source 1 | -50 - 200 °C |  | 1029 | FLOAT32 | 1 |  | 30 | 15 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | Tmp |  | mag | f | OS/SIML1$MX$Tmp$mag$f | ✔ | source_1__oil_temperature | 1030
Source 1 Ambient Temperature (°C) | Source 1 | -50 - 80 °C |  | 1031 | FLOAT32 | 1 |  | 30 | 16 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | AmbTmp |  | mag | f | OS/SIML1$MX$AmbTmp$mag$f | ✔ | source_1__ambient_temperature | 1032
Source 1 Normalization Temperature (°C) | Source 1 | 0 - 20 °C |  | 1033 | FLOAT32 | 1 |  | 30 | 17 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | NorTmp |  | mag | f | OS/SIML1$MX$NorTmp$mag$f | ✔ | source_1__norm_temperature | 1034
Source 1 RS (%) (Relative Saturation) | Source 1 | 0 - 100 % |  | 1035 | FLOAT32 | 1 |  | 30 | 18 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | H2O |  | mag | f | OS/SIML1$MX$H2O$mag$f | ✔ | source_1__relative_saturation | 1036
Source 1 RCDCM (Ratio of CO2 and CO Calculated) | Source 1 | 0 - 10,000 |  | 1037 | FLOAT32 | 1 |  | 30 | 19 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | RCDCM |  | mag | f | OS/SIML1$MX$RCDCM$mag$f | ✔ | source_1__rcdcm | 1038
Source 1 H2 ROC (ppm/day) (Rate Of Change) | Source 1 | -5,000 - 5,000 ppm/day |  | 1999 | FLOAT32 | 1 |  | 30 | 1000 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | H2Rte |  | mag | f | OS/SIML1$MX$H2Rte$mag$f | ✔ | source_1__h2__roc | 2000
Source 1 CO2 ROC (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 2001 | FLOAT32 | 1 |  | 30 | 1001 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | CO2Rte |  | mag | f | OS/SIML1$MX$CO2Rte$mag$f | ✔ | source_1__co2__roc | 2002
Source 1 CO ROC (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 2003 | FLOAT32 | 1 |  | 30 | 1002 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | CORte |  | mag | f | OS/SIML1$MX$CORte$mag$f | ✔ | source_1__co__roc | 2004
Source 1 C2H4 ROC (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 2005 | FLOAT32 | 1 |  | 30 | 1003 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | C2H4Rte |  | mag | f | OS/SIML1$MX$C2H4Rte$mag$f | ✔ | source_1__c2h4__roc | 2006
Source 1 C2H6 ROC (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 2007 | FLOAT32 | 1 |  | 30 | 1004 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | C2H6Rte |  | mag | f | OS/SIML1$MX$C2H6Rte$mag$f | ✔ | source_1__c2h6__roc | 2008
Source 1 CH4 ROC (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 2009 | FLOAT32 | 1 |  | 30 | 1005 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | CH4Rte |  | mag | f | OS/SIML1$MX$CH4Rte$mag$f | ✔ | source_1__ch4__roc | 2010
Source 1 C2H2 ROC (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 2011 | FLOAT32 | 1 |  | 30 | 1006 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | C2H2Rte |  | mag | f | OS/SIML1$MX$C2H2Rte$mag$f | ✔ | source_1__c2h2__roc | 2012
Source 1 H2O ROC (ppm/day) | Source 1 | -10,000 - 10,000 ppm/day |  | 2013 | FLOAT32 | 1 |  | 30 | 1007 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | MstRte |  | mag | f | OS/SIML1$MX$MstRte$mag$f | ✔ | source_1__h2o__roc | 2014
Source 1 O2 ROC (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 2015 | FLOAT32 | 1 |  | 30 | 1008 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | O2Rte |  | mag | f | OS/SIML1$MX$O2Rte$mag$f | ✔ | source_1__o2__roc | 2016
Source 1 TDCG ROC (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 2017 | FLOAT32 | 1 |  | 30 | 1009 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | CgRte |  | mag | f | OS/SIML1$MX$CgRte$mag$f | ✔ | source_1__tdcg__roc | 2018
Source 1 N2 ROC (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 2019 | FLOAT32 | 1 |  | 30 | 1010 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | N2Rte |  | mag | f | OS/SIML1$MX$N2Rte$mag$f | ✔ | source_1__n2__roc | 2020
Source 1 RCDCM ROC (Ratio of CO2 and CO Calculated) | Source 1 | -10,000 - 10,000 |  | 2021 | FLOAT32 | 1 |  | 30 | 1011 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | RCDCMRte |  | mag | f | OS/SIML1$MX$RCDCMRte$mag$f | ✔ | source_1__rcdcm__roc | 2022
Source 1 TDG ROC | Source 1 | -100,000 -100,000 ppm/day |  | 2023 | FLOAT32 | 1 |  | 30 | 1012 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | FullGasRte |  | mag | f | OS/SIML1$MX$FullGasRte$mag$f | ✔ | source_1__tdg__roc | 2024
Source 1 TDH ROC | Source 1 | -100,000 -100,000 ppm/day |  | 2025 | FLOAT32 | 1 |  | 30 | 1013 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | HCGasRte |  | mag | f | OS/SIML1$MX$HCGasRte$mag$f | ✔ | source_1__tdh__roc | 2026
Source 1 RS ROC | Source 1 | -100 - 100 % |  | 2027 | FLOAT32 | 1 |  | 30 | 1014 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | H2ORte |  | mag | f | OS/SIML1$MX$H2ORte$mag$f | ✔ | source_1__relative_saturation__roc | 2028
Source 1 Ratio 1 (user defined) | Source 1 | 0 - 10,000 |  | 2499 | FLOAT32 | 1 |  | 30 | 1500 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | Ratio1 |  | mag | f | OS/SIML1$MX$Ratio1$mag$f | ✔ | source_1__ratio_1 | 2500
Source 1 Ratio 2 (user defined) | Source 1 | 0 - 10,000 |  | 2501 | FLOAT32 | 1 |  | 30 | 1501 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | Ratio2 |  | mag | f | OS/SIML1$MX$Ratio2$mag$f | ✔ | source_1__ratio_2 | 2502
Source 1 Ratio 3 (user defined) | Source 1 | 0 - 10,000 |  | 2503 | FLOAT32 | 1 |  | 30 | 1502 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | Ratio3 |  | mag | f | OS/SIML1$MX$Ratio3$mag$f | ✔ | source_1__ratio_3 | 2504
Source 1 Ratio 4 (user defined) | Source 1 | 0 - 10,000 |  | 2505 | FLOAT32 | 1 |  | 30 | 1503 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | Ratio4 |  | mag | f | OS/SIML1$MX$Ratio4$mag$f | ✔ | source_1__ratio_4 | 2506
Source 1 Ratio 5 (user defined) | Source 1 | 0 - 10,000 |  | 2507 | FLOAT32 | 1 |  | 30 | 1504 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | Ratio5 |  | mag | f | OS/SIML1$MX$Ratio5$mag$f | ✔ | source_1__ratio_5 | 2508
Analogue Input 1 (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 2509 | FLOAT32 | 1 |  | 30 | 1505 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn1 |  | mag | f | OS/GGIO1$MX$AnIn1$mag$f | ✔ | ain_1 | 2510
Analogue Input 2 (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 2511 | FLOAT32 | 1 |  | 30 | 1506 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn2 |  | mag | f | OS/GGIO1$MX$AnIn2$mag$f | ✔ | ain_2 | 2512
Analogue Input 3 (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 2513 | FLOAT32 | 1 |  | 30 | 1507 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn3 |  | mag | f | OS/GGIO1$MX$AnIn3$mag$f | ✔ | ain_3 | 2514
Analogue Input 4 (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 2515 | FLOAT32 | 1 |  | 30 | 1508 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn4 |  | mag | f | OS/GGIO1$MX$AnIn4$mag$f | ✔ | ain_4 | 2516
Analogue Input 5 (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 2517 | FLOAT32 | 1 |  | 30 | 1509 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn5 |  | mag | f | OS/GGIO1$MX$AnIn5$mag$f | ✔ | ain_5 | 2518
Analogue Input 6 (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 2519 | FLOAT32 | 1 |  | 30 | 1510 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn6 |  | mag | f | OS/GGIO1$MX$AnIn6$mag$f | ✔ | ain_6 | 2520
Source 1 Ratio 6 (user defined) | Source 1 | 0 – 10,000 |  | 2521 | FLOAT32 | 1 |  | 30 | 1511 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | Ratio6 |  | mag | f | OS/SIML1$MX$Ratio6$mag$f | ✔ | source_1__ratio_6 | 2522
Source 1 Ratio 7 (user defined) | Source 1 | 0 – 10,000 |  | 2523 | FLOAT32 | 1 |  | 30 | 1512 | 2 | 5 | 7 | ✔ | Active |  | OS | SIML1 | MX | Ratio7 |  | mag | f | OS/SIML1$MX$Ratio7$mag$f | ✔ | source_1__ratio_7 | 2524
Analogue Input 7 (user defined units) | General | -4,294,967,295 - 4,294,967,295 |  | 2599 | FLOAT32 | 1 |  | 30 | 1600 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn7 |  | mag | f | OS/GGIO1$MX$AnIn7$mag$f | ✔ | ain_7 | 2600
Analogue Input 8 (user defined units) | General | -4,294,967,295 - 4,294,967,295 |  | 2601 | FLOAT32 | 1 |  | 30 | 1601 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn8 |  | mag | f | OS/GGIO1$MX$AnIn8$mag$f | ✔ | ain_8 | 2602
Analogue Input 9 (user defined units) | General | -4,294,967,295 - 4,294,967,295 |  | 2603 | FLOAT32 | 1 |  | 30 | 1602 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn9 |  | mag | f | OS/GGIO1$MX$AnIn9$mag$f | ✔ | ain_9 | 2604
Analogue Input 10 (user defined units) | General | -4,294,967,295 - 4,294,967,295 |  | 2605 | FLOAT32 | 1 |  | 30 | 1603 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn10 |  | mag | f | OS/GGIO1$MX$AnIn10$mag$f | ✔ | ain_10 | 2606
Analogue Input 11 (user defined units) | General | -4,294,967,295 - 4,294,967,295 |  | 2607 | FLOAT32 | 1 |  | 30 | 1604 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn11 |  | mag | f | OS/GGIO1$MX$AnIn11$mag$f | ✔ | ain_11 | 2608
Analogue Input 12 (user defined units) | General | -4,294,967,295 - 4,294,967,295 |  | 2609 | FLOAT32 | 1 |  | 30 | 1605 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn12 |  | mag | f | OS/GGIO1$MX$AnIn12$mag$f | ✔ | ain_12 | 2610
Analogue Input 13 (user defined units) | General | -4,294,967,295 - 4,294,967,295 |  | 2611 | FLOAT32 | 1 |  | 30 | 1606 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn13 |  | mag | f | OS/GGIO1$MX$AnIn13$mag$f | ✔ | ain_13 | 2612
Analogue Input 14 (user defined units) | General | -4,294,967,295 - 4,294,967,295 |  | 2613 | FLOAT32 | 1 |  | 30 | 1607 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn14 |  | mag | f | OS/GGIO1$MX$AnIn14$mag$f | ✔ | ain_14 | 2614
Analogue Input 15 (user defined units) | General | -4,294,967,295 - 4,294,967,295 |  | 2615 | FLOAT32 | 1 |  | 30 | 1608 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn15 |  | mag | f | OS/GGIO1$MX$AnIn15$mag$f | ✔ | ain_15 | 2616
Analogue Input 16 (user defined units) | General | -4,294,967,295 - 4,294,967,295 |  | 2617 | FLOAT32 | 1 |  | 30 | 1609 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn16 |  | mag | f | OS/GGIO1$MX$AnIn16$mag$f | ✔ | ain_16 | 2618
Analogue Input 17 (user defined units) | General | -4,294,967,295 - 4,294,967,295 |  | 2619 | FLOAT32 | 1 |  | 30 | 1610 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn17 |  | mag | f | OS/GGIO1$MX$AnIn17$mag$f | ✔ | ain_17 | 2620
Analogue Input 18 (user defined units) | General | -4,294,967,295 - 4,294,967,295 |  | 2621 | FLOAT32 | 1 |  | 30 | 1611 | 2 | 5 | 7 | ✔ | Active |  | OS | GGIO1 | MX | AnIn18 |  | mag | f | OS/GGIO1$MX$AnIn18$mag$f | ✔ | ain_18 | 2622
TransOpto Channel 1 Temperature (°C) | Trans Opto | -80 – 250 °C |  | 2999 | FLOAT32 | 1 |  | 30 | 2000 | 2 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp1 |  | instMag | f | OS/TTMP1$MX$Tmp1$instMag$f | ✔ | to_temperature_1 | 3000
TransOpto Channel 2 Temperature (°C) | Trans Opto | -80 – 250 °C |  | 3001 | FLOAT32 | 1 |  | 30 | 2001 | 2 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp2 |  | instMag | f | OS/TTMP1$MX$Tmp2$instMag$f | ✔ | to_temperature_2 | 3002
TransOpto Channel 3 Temperature (°C) | Trans Opto | -80 – 250 °C |  | 3003 | FLOAT32 | 1 |  | 30 | 2002 | 2 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp3 |  | instMag | f | OS/TTMP1$MX$Tmp3$instMag$f | ✔ | to_temperature_3 | 3004
TransOpto Channel 4 Temperature (°C) | Trans Opto | -80 – 250 °C |  | 3005 | FLOAT32 | 1 |  | 30 | 2003 | 2 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp4 |  | instMag | f | OS/TTMP1$MX$Tmp4$instMag$f | ✔ | to_temperature_4 | 3006
TransOpto Channel 5 Temperature (°C) | Trans Opto | -80 – 250 °C |  | 3007 | FLOAT32 | 1 |  | 30 | 2004 | 2 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp5 |  | instMag | f | OS/TTMP1$MX$Tmp5$instMag$f | ✔ | to_temperature_5 | 3008
TransOpto Channel 6 Temperature (°C) | Trans Opto | -80 – 250 °C |  | 3009 | FLOAT32 | 1 |  | 30 | 2005 | 2 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp6 |  | instMag | f | OS/TTMP1$MX$Tmp6$instMag$f | ✔ | to_temperature_6 | 3010
TransOpto Channel 7 Temperature (°C) | Trans Opto | -80 – 250 °C |  | 3011 | FLOAT32 | 1 |  | 30 | 2006 | 2 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp7 |  | instMag | f | OS/TTMP1$MX$Tmp7$instMag$f | ✔ | to_temperature_7 | 3012
TransOpto Channel 8 Temperature (°C) | Trans Opto | -80 – 250 °C |  | 3013 | FLOAT32 | 1 |  | 30 | 2007 | 2 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp8 |  | instMag | f | OS/TTMP1$MX$Tmp8$instMag$f | ✔ | to_temperature_8 | 3014
TransOpto Channel 1 Temperature ROC (°C/day) | Trans Opto | -250 – 250 °C/day |  | 3999 | FLOAT32 | 1 |  | 30 | 3000 | 2 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte1 |  | mag | f | OS/TTMP1$MX$TmpRte1$mag$f | ✔ | to_temperature_1__roc | 4000
TransOpto Channel 2 Temperature ROC (°C/day) | Trans Opto | -250 – 250 °C/day |  | 4001 | FLOAT32 | 1 |  | 30 | 3001 | 2 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte2 |  | mag | f | OS/TTMP1$MX$TmpRte2$mag$f | ✔ | to_temperature_2__roc | 4002
TransOpto Channel 3 Temperature ROC (°C/day) | Trans Opto | -250 – 250 °C/day |  | 4003 | FLOAT32 | 1 |  | 30 | 3002 | 2 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte3 |  | mag | f | OS/TTMP1$MX$TmpRte3$mag$f | ✔ | to_temperature_3__roc | 4004
TransOpto Channel 4 Temperature ROC (°C/day) | Trans Opto | -250 – 250 °C/day |  | 4005 | FLOAT32 | 1 |  | 30 | 3003 | 2 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte4 |  | mag | f | OS/TTMP1$MX$TmpRte4$mag$f | ✔ | to_temperature_4__roc | 4006
TransOpto Channel 5 Temperature ROC (°C/day) | Trans Opto | -250 – 250 °C/day |  | 4007 | FLOAT32 | 1 |  | 30 | 3004 | 2 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte5 |  | mag | f | OS/TTMP1$MX$TmpRte5$mag$f | ✔ | to_temperature_5__roc | 4008
TransOpto Channel 6 Temperature ROC (°C/day) | Trans Opto | -250 – 250 °C/day |  | 4009 | FLOAT32 | 1 |  | 30 | 3005 | 2 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte6 |  | mag | f | OS/TTMP1$MX$TmpRte6$mag$f | ✔ | to_temperature_6__roc | 4010
TransOpto Channel 7 Temperature ROC (°C/day) | Trans Opto | -250 – 250 °C/day |  | 4011 | FLOAT32 | 1 |  | 30 | 3006 | 2 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte7 |  | mag | f | OS/TTMP1$MX$TmpRte7$mag$f | ✔ | to_temperature_7__roc | 4012
TransOpto Channel 8 Temperature ROC (°C/day) | Trans Opto | -250 – 250 °C/day |  | 4013 | FLOAT32 | 1 |  | 30 | 3007 | 2 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte8 |  | mag | f | OS/TTMP1$MX$TmpRte8$mag$f | ✔ | to_temperature_8__roc | 4014
Source 1 H2 High-High Alarm Limit (ppm) | Source 1 | 5 - 5,000 ppm |  | 4999 | FLOAT32 | 1 |  | 30 | 4000 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | H2Als |  | mag | f | OS/SIML1$MX$H2Als$mag$f | ✔ | source_1__h2__high_high__limit | 5000
Source 1 H2 High Alarm Limit (ppm) | Source 1 | 5 - 5,000 ppm |  | 5001 | FLOAT32 | 1 |  | 30 | 4001 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | H2Wrs |  | mag | f | OS/SIML1$MX$H2Wrs$mag$f | ✔ | source_1__h2__high__limit | 5002
Source 1 CO2 High-High Alarm Limit (ppm) | Source 1 | 20 - 50,000 ppm |  | 5003 | FLOAT32 | 1 |  | 30 | 4002 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | CO2Als |  | mag | f | OS/SIML1$MX$CO2Als$mag$f | ✔ | source_1__co2__high_high__limit | 5004
Source 1 CO2 High Alarm Limit (ppm) | Source 1 | 20 - 50,000 ppm |  | 5005 | FLOAT32 | 1 |  | 30 | 4003 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | CO2Wrs |  | mag | f | OS/SIML1$MX$CO2Wrs$mag$f | ✔ | source_1__co2__high__limit | 5006
Source 1 CO High-High Alarm Limit (ppm) | Source 1 | 1 - 50,000 ppm |  | 5007 | FLOAT32 | 1 |  | 30 | 4004 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | COAls |  | mag | f | OS/SIML1$MX$COAls$mag$f | ✔ | source_1__co__high_high__limit | 5008
Source 1 CO High Alarm Limit (ppm) | Source 1 | 1 - 50,000 ppm |  | 5009 | FLOAT32 | 1 |  | 30 | 4005 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | COWrs |  | mag | f | OS/SIML1$MX$COWrs$mag$f | ✔ | source_1__co__high__limit | 5010
Source 1 C2H4 High-High Alarm Limit (ppm) | Source 1 | 1 - 50,000 ppm |  | 5011 | FLOAT32 | 1 |  | 30 | 4006 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | C2H4Als |  | mag | f | OS/SIML1$MX$C2H4Als$mag$f | ✔ | source_1__c2h4__high_high__limit | 5012
Source 1 C2H4 High Alarm Limit (ppm) | Source 1 | 1 - 50,000 ppm |  | 5013 | FLOAT32 | 1 |  | 30 | 4007 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | C2H4Wrs |  | mag | f | OS/SIML1$MX$C2H4Wrs$mag$f | ✔ | source_1__c2h4__high__limit | 5014
Source 1 C2H6 High-High Alarm Limit (ppm) | Source 1 | 1 - 50,000 ppm |  | 5015 | FLOAT32 | 1 |  | 30 | 4008 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | C2H6Als |  | mag | f | OS/SIML1$MX$C2H6Als$mag$f | ✔ | source_1__c2h6__high_high__limit | 5016
Source 1 C2H6 High Alarm Limit (ppm) | Source 1 | 1 - 50,000 ppm |  | 5017 | FLOAT32 | 1 |  | 30 | 4009 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | C2H6Wrs |  | mag | f | OS/SIML1$MX$C2H6Wrs$mag$f | ✔ | source_1__c2h6__high__limit | 5018
Source 1 CH4 High-High Alarm Limit (ppm) | Source 1 | 2 - 50,000 ppm |  | 5019 | FLOAT32 | 1 |  | 30 | 4010 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | CH4Als |  | mag | f | OS/SIML1$MX$CH4Als$mag$f | ✔ | source_1__ch4__high_high__limit | 5020
Source 1 CH4 High Alarm Limit (ppm) | Source 1 | 2 - 50,000 ppm |  | 5021 | FLOAT32 | 1 |  | 30 | 4011 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | CH4Wrs |  | mag | f | OS/SIML1$MX$CH4Wrs$mag$f | ✔ | source_1__ch4__high__limit | 5022
Source 1 C2H2 High-High Alarm Limit (ppm) | Source 1 | 0.5 - 50,000 ppm |  | 5023 | FLOAT32 | 1 |  | 30 | 4012 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | C2H2Als |  | mag | f | OS/SIML1$MX$C2H2Als$mag$f | ✔ | source_1__c2h2__high_high__limit | 5024
Source 1 C2H2 High Alarm Limit (ppm) | Source 1 | 0.5 - 50,000 ppm |  | 5025 | FLOAT32 | 1 |  | 30 | 4013 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | C2H2Wrs |  | mag | f | OS/SIML1$MX$C2H2Wrs$mag$f | ✔ | source_1__c2h2__high__limit | 5026
Source 1 H2O High-High Alarm Limit (ppm) | Source 1 | 0 - 10,000 ppm |  | 5027 | FLOAT32 | 1 |  | 30 | 4014 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | MstAls |  | mag | f | OS/SIML1$MX$MstAls$mag$f | ✔ | source_1__h2o__high_high__limit | 5028
Source 1 H2O High Alarm Limit (ppm) | Source 1 | 0 - 10,000 ppm |  | 5029 | FLOAT32 | 1 |  | 30 | 4015 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | MstWrs |  | mag | f | OS/SIML1$MX$MstWrs$mag$f | ✔ | source_1__h2o__high__limit | 5030
Source 1 O2 High-High Alarm Limit (ppm) | Source 1 | 100 - 50,000 ppm |  | 5031 | FLOAT32 | 1 |  | 30 | 4016 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | O2Als |  | mag | f | OS/SIML1$MX$O2Als$mag$f | ✔ | source_1__o2__high_high__limit | 5032
Source 1 O2 High Alarm Limit (ppm) | Source 1 | 100 - 50,000 ppm |  | 5033 | FLOAT32 | 1 |  | 30 | 4017 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | O2Wrs |  | mag | f | OS/SIML1$MX$O2Wrs$mag$f | ✔ | source_1__o2__high__limit | 5034
Source 1 TDCG High-High Alarm Limit (ppm) | Source 1 | 0 - 50,000 ppm |  | 5035 | FLOAT32 | 1 |  | 30 | 4018 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | CgAls |  | mag | f | OS/SIML1$MX$CgAls$mag$f | ✔ | source_1__tdcg__high_high__limit | 5036
Source 1 TDCG High Alarm Limit (ppm) | Source 1 | 0 - 50,000 ppm |  | 5037 | FLOAT32 | 1 |  | 30 | 4019 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | CgWrs |  | mag | f | OS/SIML1$MX$CgWrs$mag$f | ✔ | source_1__tdcg__high__limit | 5038
Source 1 N2 High-High Alarm Limit (ppm) | Source 1 | 10,000 - 50,000 ppm |  | 5039 | FLOAT32 | 1 |  | 30 | 4020 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | N2Als |  | mag | f | OS/SIML1$MX$N2Als$mag$f | ✔ | source_1__n2__high_high__limit | 5040
Source 1 N2 High Alarm Limit (ppm) | Source 1 | 10,000 - 50,000 ppm |  | 5041 | FLOAT32 | 1 |  | 30 | 4021 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | N2Wrs |  | mag | f | OS/SIML1$MX$N2Wrs$mag$f | ✔ | source_1__n2__high__limit | 5042
Source 1 RS High-High Alarm Limit (%) | Source 1 | 0 -100 RS % |  | 5043 | FLOAT32 | 1 |  | 30 | 4022 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | H2OAls |  | mag | f | OS/SIML1$MX$H2OAls$mag$f | ✔ | source_1__relative_saturation__high_high__limit | 5044
Source 1 RS High Alarm Limit (%) | Source 1 | 0 -100 RS % |  | 5045 | FLOAT32 | 1 |  | 30 | 4023 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | H2OWrs |  | mag | f | OS/SIML1$MX$H2OWrs$mag$f | ✔ | source_1__relative_saturation__high__limit | 5046
Source 1 H2 ROC High-High Alarm Limit (ppm/day) | Source 1 | -5,000 - 5,000 ppm/day |  | 5499 | FLOAT32 | 1 |  | 30 | 4500 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | H2RteAls |  | mag | f | OS/SIML1$MX$H2RteAls$mag$f | ✔ | source_1__h2__roc__high_high__limit | 5500
Source 1 H2 ROC High Alarm Limit (ppm/day) | Source 1 | -5,000 - 5,000 ppm/day |  | 5501 | FLOAT32 | 1 |  | 30 | 4501 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | H2RteWrs |  | mag | f | OS/SIML1$MX$H2RteWrs$mag$f | ✔ | source_1__h2__roc__high__limit | 5502
Source 1 CO2 ROC High-High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5503 | FLOAT32 | 1 |  | 30 | 4502 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | CO2RteAls |  | mag | f | OS/SIML1$MX$CO2RteAls$mag$f | ✔ | source_1__co2__roc__high_high__limit | 5504
Source 1 CO2 ROC High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5505 | FLOAT32 | 1 |  | 30 | 4503 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | CO2RteWrs |  | mag | f | OS/SIML1$MX$CO2RteWrs$mag$f | ✔ | source_1__co2__roc__high__limit | 5506
Source 1 CO ROC High-High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5507 | FLOAT32 | 1 |  | 30 | 4504 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | CORteAls |  | mag | f | OS/SIML1$MX$CORteAls$mag$f | ✔ | source_1__co__roc__high_high__limit | 5508
Source 1 CI ROC High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5509 | FLOAT32 | 1 |  | 30 | 4505 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | CORteWrs |  | mag | f | OS/SIML1$MX$CORteWrs$mag$f | ✔ | source_1__co__roc__high__limit | 5510
Source 1 C2H4 ROC High-High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5511 | FLOAT32 | 1 |  | 30 | 4506 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | C2H4RteAls |  | mag | f | OS/SIML1$MX$C2H4RteAls$mag$f | ✔ | source_1__c2h4__roc__high_high__limit | 5512
Source 1 C2H4 ROC High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5513 | FLOAT32 | 1 |  | 30 | 4507 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | C2H4RteWrs |  | mag | f | OS/SIML1$MX$C2H4RteWrs$mag$f | ✔ | source_1__c2h4__roc__high__limit | 5514
Source 1 C2H6 ROC High-High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5515 | FLOAT32 | 1 |  | 30 | 4508 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | C2H6RteAls |  | mag | f | OS/SIML1$MX$C2H6RteAls$mag$f | ✔ | source_1__c2h6__roc__high_high__limit | 5516
Source 1 C2H6 ROC High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5517 | FLOAT32 | 1 |  | 30 | 4509 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | C2H6RteWrs |  | mag | f | OS/SIML1$MX$C2H6RteWrs$mag$f | ✔ | source_1__c2h6__roc__high__limit | 5518
Source 1 CH4 ROC High-High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5519 | FLOAT32 | 1 |  | 30 | 4510 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | CH4RteAls |  | mag | f | OS/SIML1$MX$CH4RteAls$mag$f | ✔ | source_1__ch4__roc__high_high__limit | 5520
Source 1 CH4 ROC High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5521 | FLOAT32 | 1 |  | 30 | 4511 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | CH4RteWrs |  | mag | f | OS/SIML1$MX$CH4RteWrs$mag$f | ✔ | source_1__ch4__roc__high__limit | 5522
Source 1 C2H2 ROC High-High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5523 | FLOAT32 | 1 |  | 30 | 4512 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | C2H2RteAls |  | mag | f | OS/SIML1$MX$C2H2RteAls$mag$f | ✔ | source_1__c2h2__roc__high_high__limit | 5524
Source 1 C2H2 ROC High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5525 | FLOAT32 | 1 |  | 30 | 4513 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | C2H2RteWrs |  | mag | f | OS/SIML1$MX$C2H2RteWrs$mag$f | ✔ | source_1__c2h2__roc__high__limit | 5526
Source 1 H2O ROC High-High Alarm Limit (ppm/day) | Source 1 | -10,000 - 10,000 ppm/day |  | 5527 | FLOAT32 | 1 |  | 30 | 4514 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | MstRteAls |  | mag | f | OS/SIML1$MX$MstRteAls$mag$f | ✔ | source_1__h2o__roc__high_high__limit | 5528
Source 1 H2O ROC High Alarm Limit (ppm/day) | Source 1 | -10,000 - 10,000 ppm/day |  | 5529 | FLOAT32 | 1 |  | 30 | 4515 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | MstRteWrs |  | mag | f | OS/SIML1$MX$MstRteWrs$mag$f | ✔ | source_1__h2o__roc__high__limit | 5530
Source 1 O2 ROC High-High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5531 | FLOAT32 | 1 |  | 30 | 4516 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | O2RteAls |  | mag | f | OS/SIML1$MX$O2RteAls$mag$f | ✔ | source_1__o2__roc__high_high__limit | 5532
Source 1 O2 ROC High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5533 | FLOAT32 | 1 |  | 30 | 4517 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | O2RteWrs |  | mag | f | OS/SIML1$MX$O2RteWrs$mag$f | ✔ | source_1__o2__roc__high__limit | 5534
Source 1 TDCG ROC High-High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5535 | FLOAT32 | 1 |  | 30 | 4518 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | CgRteAls |  | mag | f | OS/SIML1$MX$CgRteAls$mag$f | ✔ | source_1__tdcg__roc__high_high__limit | 5536
Source 1 TDCG ROC High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5537 | FLOAT32 | 1 |  | 30 | 4519 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | CgRteWrs |  | mag | f | OS/SIML1$MX$CgRteWrs$mag$f | ✔ | source_1__tdcg__roc__high__limit | 5538
Source 1 N2 ROC High-High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5539 | FLOAT32 | 1 |  | 30 | 4520 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | N2RteAls |  | mag | f | OS/SIML1$MX$N2RteAls$mag$f | ✔ | source_1__n2__roc__high_high__limit | 5540
Source 1 N2 ROC High Alarm Limit (ppm/day) | Source 1 | -50,000 - 50,000 ppm/day |  | 5541 | FLOAT32 | 1 |  | 30 | 4521 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | N2RteWrs |  | mag | f | OS/SIML1$MX$N2RteWrs$mag$f | ✔ | source_1__n2__roc__high__limit | 5542
Source 1 RCDCM ROC High-High Alarm Limit (Ratio of CO2 and CO Calculated) | Source 1 | -10,000 - 10,000 |  | 5543 | FLOAT32 | 1 |  | 30 | 4522 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | RCDCMAlsH |  | mag | f | OS/SIML1$MX$RCDCMAlsH$mag$f | ✔ | source_1__rcdcm__roc__high_high__limit | 5544
Source 1 RCDCM ROC High Alarm Limit (Ratio of CO2 and CO Calculated) | Source 1 | -10,000 - 10,000 |  | 5545 | FLOAT32 | 1 |  | 30 | 4523 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | RCDCMWrsH |  | mag | f | OS/SIML1$MX$RCDCMWrsH$mag$f | ✔ | source_1__rcdcm__roc__high__limit | 5546
Source 1 RCDCM ROC Low Alarm Limit (Ratio of CO2 and CO Calculated) | Source 1 | -10,000 - 10,000 |  | 5547 | FLOAT32 | 1 |  | 30 | 4524 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | RCDCMWrsL |  | mag | f | OS/SIML1$MX$RCDCMWrsL$mag$f | ✔ | source_1__rcdcm__roc__low__limit | 5548
Source 1 RCDCM ROC Low-Low Alarm Limit (Ratio of CO2 and CO Calculated) | Source 1 | -10,000 - 10,000 |  | 5549 | FLOAT32 | 1 |  | 30 | 4525 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | RCDCMAlsL |  | mag | f | OS/SIML1$MX$RCDCMAlsL$mag$f | ✔ | source_1__rcdcm__roc__low_low__limit | 5550
Source 1 Ratio 1 High-High Alarm Limit | Source 1 | -10,000 - 10,000 |  | 5999 | FLOAT32 | 1 |  | 30 | 5000 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat1AlsH |  | mag | f | OS/SIML1$MX$Rat1AlsH$mag$f | ✔ | source_1__ratio_1__high_high__limit | 6000
Source 1 Ratio 1 High Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6001 | FLOAT32 | 1 |  | 30 | 5001 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat1WrsH |  | mag | f | OS/SIML1$MX$Rat1WrsH$mag$f | ✔ | source_1__ratio_1__high__limit | 6002
Source 1 Ratio 1 Low Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6003 | FLOAT32 | 1 |  | 30 | 5002 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat1WrsL |  | mag | f | OS/SIML1$MX$Rat1WrsL$mag$f | ✔ | source_1__ratio_1__low__limit | 6004
Source 1 Ratio 1 Low-Low Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6005 | FLOAT32 | 1 |  | 30 | 5003 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat1AlsL |  | mag | f | OS/SIML1$MX$Rat1AlsL$mag$f | ✔ | source_1__ratio_1__low_low__limit | 6006
Source 1 Ratio 2 High-High Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6007 | FLOAT32 | 1 |  | 30 | 5004 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat2AlsH |  | mag | f | OS/SIML1$MX$Rat2AlsH$mag$f | ✔ | source_1__ratio_2__high_high__limit | 6008
Source 1 Ratio 2 High Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6009 | FLOAT32 | 1 |  | 30 | 5005 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat2WrsH |  | mag | f | OS/SIML1$MX$Rat2WrsH$mag$f | ✔ | source_1__ratio_2__high__limit | 6010
Source 1 Ratio 2 Low Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6011 | FLOAT32 | 1 |  | 30 | 5006 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat2WrsL |  | mag | f | OS/SIML1$MX$Rat2WrsL$mag$f | ✔ | source_1__ratio_2__low__limit | 6012
Source 1 Ratio 2 Low-Low Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6013 | FLOAT32 | 1 |  | 30 | 5007 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat2AlsL |  | mag | f | OS/SIML1$MX$Rat2AlsL$mag$f | ✔ | source_1__ratio_2__low_low__limit | 6014
Source 1 Ratio 3 High-High Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6015 | FLOAT32 | 1 |  | 30 | 5008 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat3AlsH |  | mag | f | OS/SIML1$MX$Rat3AlsH$mag$f | ✔ | source_1__ratio_3__high_high__limit | 6016
Source 1 Ratio 3 High Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6017 | FLOAT32 | 1 |  | 30 | 5009 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat3WrsH |  | mag | f | OS/SIML1$MX$Rat3WrsH$mag$f | ✔ | source_1__ratio_3__high__limit | 6018
Source 1 Ratio 3 Low Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6019 | FLOAT32 | 1 |  | 30 | 5010 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat3WrsL |  | mag | f | OS/SIML1$MX$Rat3WrsL$mag$f | ✔ | source_1__ratio_3__low__limit | 6020
Source 1 Ratio 3 Low-Low Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6021 | FLOAT32 | 1 |  | 30 | 5011 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat3AlsL |  | mag | f | OS/SIML1$MX$Rat3AlsL$mag$f | ✔ | source_1__ratio_3__low_low__limit | 6022
Source 1 Ratio 4 High-High Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6023 | FLOAT32 | 1 |  | 30 | 5012 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat4AlsH |  | mag | f | OS/SIML1$MX$Rat4AlsH$mag$f | ✔ | source_1__ratio_4__high_high__limit | 6024
Source 1 Ratio 4 High Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6025 | FLOAT32 | 1 |  | 30 | 5013 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat4WrsH |  | mag | f | OS/SIML1$MX$Rat4WrsH$mag$f | ✔ | source_1__ratio_4__high__limit | 6026
Source 1 Ratio 4 Low Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6027 | FLOAT32 | 1 |  | 30 | 5014 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat4WrsL |  | mag | f | OS/SIML1$MX$Rat4WrsL$mag$f | ✔ | source_1__ratio_4__low__limit | 6028
Source 1 Ratio 4 Low-Low Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6029 | FLOAT32 | 1 |  | 30 | 5015 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat4AlsL |  | mag | f | OS/SIML1$MX$Rat4AlsL$mag$f | ✔ | source_1__ratio_4__low_low__limit | 6030
Source 1 Ratio 5 High-High Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6031 | FLOAT32 | 1 |  | 30 | 5016 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat5AlsH |  | mag | f | OS/SIML1$MX$Rat5AlsH$mag$f | ✔ | source_1__ratio_5__high_high__limit | 6032
Source 1 Ratio 5 High Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6033 | FLOAT32 | 1 |  | 30 | 5017 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat5WrsH |  | mag | f | OS/SIML1$MX$Rat5WrsH$mag$f | ✔ | source_1__ratio_5__high__limit | 6034
Source 1 Ratio 5 Low Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6035 | FLOAT32 | 1 |  | 30 | 5018 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat5WrsL |  | mag | f | OS/SIML1$MX$Rat5WrsL$mag$f | ✔ | source_1__ratio_5__low__limit | 6036
Source 1 Ratio 5 Low-Low Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6037 | FLOAT32 | 1 |  | 30 | 5019 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat5AlsL |  | mag | f | OS/SIML1$MX$Rat5AlsL$mag$f | ✔ | source_1__ratio_5__low_low__limit | 6038
Source 1 Ratio 6 High-High Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6039 | FLOAT32 | 1 |  | 30 | 5020 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat6AlsH |  | mag | f | OS/SIML1$MX$Rat6AlsH$mag$f | ✔ | source_1__ratio_6__high_high__limit | 6040
Source 1 Ratio 6 High Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6041 | FLOAT32 | 1 |  | 30 | 5021 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat6WrsH |  | mag | f | OS/SIML1$MX$Rat6WrsH$mag$f | ✔ | source_1__ratio_6__high__limit | 6042
Source 1 Ratio 6 Low Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6043 | FLOAT32 | 1 |  | 30 | 5022 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat6WrsL |  | mag | f | OS/SIML1$MX$Rat6WrsL$mag$f | ✔ | source_1__ratio_6__low__limit | 6044
Source 1 Ratio 6 Low-Low Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6045 | FLOAT32 | 1 |  | 30 | 5023 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat6AlsL |  | mag | f | OS/SIML1$MX$Rat6AlsL$mag$f | ✔ | source_1__ratio_6__low_low__limit | 6046
Source 1 Ratio 7 High-High Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6047 | FLOAT32 | 1 |  | 30 | 5024 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat7AlsH |  | mag | f | OS/SIML1$MX$Rat7AlsH$mag$f | ✔ | source_1__ratio_7__high_high__limit | 6048
Source 1 Ratio 7 High Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6049 | FLOAT32 | 1 |  | 30 | 5025 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat7WrsH |  | mag | f | OS/SIML1$MX$Rat7WrsH$mag$f | ✔ | source_1__ratio_7__high__limit | 6050
Source 1 Ratio 7 Low Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6051 | FLOAT32 | 1 |  | 30 | 5026 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat7WrsL |  | mag | f | OS/SIML1$MX$Rat7WrsL$mag$f | ✔ | source_1__ratio_7__low__limit | 6052
Source 1 Ratio 7 Low-Low Alarm Limit | Source 1 | -10,000 - 10,000 |  | 6053 | FLOAT32 | 1 |  | 30 | 5027 | 3 | 5 | 7 | ✔ | Disabled |  | OS | SIML1 | MX | Rat7AlsL |  | mag | f | OS/SIML1$MX$Rat7AlsL$mag$f | ✔ | source_1__ratio_7__low_low__limit | 6054
TransOpto Channel 1 Temperature High-High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 6499 | FLOAT32 | 1 |  | 30 | 5500 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp1Als |  | mag | f | OS/TTMP1$MX$Tmp1Als$mag$f | ✔ | to_temperature_1__high_high__limit | 6500
TransOpto Channel 1 Temperature High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 6501 | FLOAT32 | 1 |  | 30 | 5501 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp1Wrs |  | mag | f | OS/TTMP1$MX$Tmp1Wrs$mag$f | ✔ | to_temperature_1__high__limit | 6502
TransOpto Channel 2 Temperature High-High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 6503 | FLOAT32 | 1 |  | 30 | 5502 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp2Als |  | mag | f | OS/TTMP1$MX$Tmp2Als$mag$f | ✔ | to_temperature_2__high_high__limit | 6504
TransOpto Channel 2 Temperature High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 6505 | FLOAT32 | 1 |  | 30 | 5503 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp2Wrs |  | mag | f | OS/TTMP1$MX$Tmp2Wrs$mag$f | ✔ | to_temperature_2__high__limit | 6506
TransOpto Channel 3 Temperature High-High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 6507 | FLOAT32 | 1 |  | 30 | 5504 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp3Als |  | mag | f | OS/TTMP1$MX$Tmp3Als$mag$f | ✔ | to_temperature_3__high_high__limit | 6508
TransOpto Channel 3 Temperature High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 6509 | FLOAT32 | 1 |  | 30 | 5505 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp3Wrs |  | mag | f | OS/TTMP1$MX$Tmp3Wrs$mag$f | ✔ | to_temperature_3__high__limit | 6510
TransOpto Channel 4 Temperature High-High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 6511 | FLOAT32 | 1 |  | 30 | 5506 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp4Als |  | mag | f | OS/TTMP1$MX$Tmp4Als$mag$f | ✔ | to_temperature_4__high_high__limit | 6512
TransOpto Channel 4 Temperature High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 6513 | FLOAT32 | 1 |  | 30 | 5507 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp4Wrs |  | mag | f | OS/TTMP1$MX$Tmp4Wrs$mag$f | ✔ | to_temperature_4__high__limit | 6514
TransOpto Channel 5 Temperature High-High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 6515 | FLOAT32 | 1 |  | 30 | 5508 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp5Als |  | mag | f | OS/TTMP1$MX$Tmp5Als$mag$f | ✔ | to_temperature_5__high_high__limit | 6516
TransOpto Channel 5 Temperature High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 6517 | FLOAT32 | 1 |  | 30 | 5509 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp5Wrs |  | mag | f | OS/TTMP1$MX$Tmp5Wrs$mag$f | ✔ | to_temperature_5__high__limit | 6518
TransOpto Channel 6 Temperature High-High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 6519 | FLOAT32 | 1 |  | 30 | 5510 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp6Als |  | mag | f | OS/TTMP1$MX$Tmp6Als$mag$f | ✔ | to_temperature_6__high_high__limit | 6520
TransOpto Channel 6 Temperature High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 6521 | FLOAT32 | 1 |  | 30 | 5511 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp6Wrs |  | mag | f | OS/TTMP1$MX$Tmp6Wrs$mag$f | ✔ | to_temperature_6__high__limit | 6522
TransOpto Channel 7 Temperature High-High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 6523 | FLOAT32 | 1 |  | 30 | 5512 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp7Als |  | mag | f | OS/TTMP1$MX$Tmp7Als$mag$f | ✔ | to_temperature_7__high_high__limit | 6524
TransOpto Channel 7 Temperature High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 6525 | FLOAT32 | 1 |  | 30 | 5513 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp7Wrs |  | mag | f | OS/TTMP1$MX$Tmp7Wrs$mag$f | ✔ | to_temperature_7__high__limit | 6526
TransOpto Channel 8 Temperature High-High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 6527 | FLOAT32 | 1 |  | 30 | 5514 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp8Als |  | mag | f | OS/TTMP1$MX$Tmp8Als$mag$f | ✔ | to_temperature_8__high_high__limit | 6528
TransOpto Channel 8 Temperature High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 6529 | FLOAT32 | 1 |  | 30 | 5515 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | Tmp8Wrs |  | mag | f | OS/TTMP1$MX$Tmp8Wrs$mag$f | ✔ | to_temperature_8__high__limit | 6530
TransOpto Channel 1 Temperature ROC High-High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 6999 | FLOAT32 | 1 |  | 30 | 6000 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte1Als |  | mag | f | OS/TTMP1$MX$TmpRte1Als$mag$f | ✔ | to_temperature_1__roc__high_high__limit | 7000
TransOpto Channel 1 Temperature ROC High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 7001 | FLOAT32 | 1 |  | 30 | 6001 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte1Wrs |  | mag | f | OS/TTMP1$MX$TmpRte1Wrs$mag$f | ✔ | to_temperature_1__roc__high__limit | 7002
TransOpto Channel 2 Temperature ROC High-High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 7003 | FLOAT32 | 1 |  | 30 | 6002 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte2Als |  | mag | f | OS/TTMP1$MX$TmpRte2Als$mag$f | ✔ | to_temperature_2__roc__high_high__limit | 7004
TransOpto Channel 2 Temperature ROC High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 7005 | FLOAT32 | 1 |  | 30 | 6003 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte2Wrs |  | mag | f | OS/TTMP1$MX$TmpRte2Wrs$mag$f | ✔ | to_temperature_2__roc__high__limit | 7006
TransOpto Channel 3 Temperature ROC High-High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 7007 | FLOAT32 | 1 |  | 30 | 6004 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte3Als |  | mag | f | OS/TTMP1$MX$TmpRte3Als$mag$f | ✔ | to_temperature_3__roc__high_high__limit | 7008
TransOpto Channel 3 Temperature ROC High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 7009 | FLOAT32 | 1 |  | 30 | 6005 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte3Wrs |  | mag | f | OS/TTMP1$MX$TmpRte3Wrs$mag$f | ✔ | to_temperature_3__roc__high__limit | 7010
TransOpto Channel 4 Temperature ROC High-High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 7011 | FLOAT32 | 1 |  | 30 | 6006 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte4Als |  | mag | f | OS/TTMP1$MX$TmpRte4Als$mag$f | ✔ | to_temperature_4__roc__high_high__limit | 7012
TransOpto Channel 4 Temperature ROC High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 7013 | FLOAT32 | 1 |  | 30 | 6007 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte4Wrs |  | mag | f | OS/TTMP1$MX$TmpRte4Wrs$mag$f | ✔ | to_temperature_4__roc__high__limit | 7014
TransOpto Channel 5 Temperature ROC High-High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 7015 | FLOAT32 | 1 |  | 30 | 6008 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte5Als |  | mag | f | OS/TTMP1$MX$TmpRte5Als$mag$f | ✔ | to_temperature_5__roc__high_high__limit | 7016
TransOpto Channel 5 Temperature ROC High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 7017 | FLOAT32 | 1 |  | 30 | 6009 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte5Wrs |  | mag | f | OS/TTMP1$MX$TmpRte5Wrs$mag$f | ✔ | to_temperature_5__roc__high__limit | 7018
TransOpto Channel 6 Temperature ROC High-High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 7019 | FLOAT32 | 1 |  | 30 | 6010 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte6Als |  | mag | f | OS/TTMP1$MX$TmpRte6Als$mag$f | ✔ | to_temperature_6__roc__high_high__limit | 7020
TransOpto Channel 6 Temperature ROC High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 7021 | FLOAT32 | 1 |  | 30 | 6011 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte6Wrs |  | mag | f | OS/TTMP1$MX$TmpRte6Wrs$mag$f | ✔ | to_temperature_6__roc__high__limit | 7022
TransOpto Channel 7 Temperature ROC High-High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 7023 | FLOAT32 | 1 |  | 30 | 6012 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte7Als |  | mag | f | OS/TTMP1$MX$TmpRte7Als$mag$f | ✔ | to_temperature_7__roc__high_high__limit | 7024
TransOpto Channel 7 Temperature ROC High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 7025 | FLOAT32 | 1 |  | 30 | 6013 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte7Wrs |  | mag | f | OS/TTMP1$MX$TmpRte7Wrs$mag$f | ✔ | to_temperature_7__roc__high__limit | 7026
TransOpto Channel 8 Temperature ROC High-High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 7027 | FLOAT32 | 1 |  | 30 | 6014 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte8Als |  | mag | f | OS/TTMP1$MX$TmpRte8Als$mag$f | ✔ | to_temperature_8__roc__high_high__limit | 7028
TransOpto Channel 8 Temperature ROC High Alarm Limit (°C) | Trans Opto | -50 - 200 °C |  | 7029 | FLOAT32 | 1 |  | 30 | 6015 | 3 | 5 | 7 | ✔ | Disabled |  | OS | TTMP1 | MX | TmpRte8Wrs |  | mag | f | OS/TTMP1$MX$TmpRte8Wrs$mag$f | ✔ | to_temperature_8__roc__high__limit | 7030
Analogue Input 1 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7499 | FLOAT32 | 1 |  | 30 | 6500 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn1AlsH |  | mag | f | OS/GGIO1$MX$AnIn1AlsH$mag$f | ✔ | ain_1__high_high__limit | 7500
Analogue Input 1 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7501 | FLOAT32 | 1 |  | 30 | 6501 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn1WrsH |  | mag | f | OS/GGIO1$MX$AnIn1WrsH$mag$f | ✔ | ain_1__high__limit | 7502
Analogue Input 1 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7503 | FLOAT32 | 1 |  | 30 | 6502 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn1WrsL |  | mag | f | OS/GGIO1$MX$AnIn1WrsL$mag$f | ✔ | ain_1__low__limit | 7504
Analogue Input 1 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7505 | FLOAT32 | 1 |  | 30 | 6503 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn1AlsL |  | mag | f | OS/GGIO1$MX$AnIn1AlsL$mag$f | ✔ | ain_1__low_low__limit | 7506
Analogue Input 2 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7507 | FLOAT32 | 1 |  | 30 | 6504 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn2AlsH |  | mag | f | OS/GGIO1$MX$AnIn2AlsH$mag$f | ✔ | ain_2__high_high__limit | 7508
Analogue Input 2 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7509 | FLOAT32 | 1 |  | 30 | 6505 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn2WrsH |  | mag | f | OS/GGIO1$MX$AnIn2WrsH$mag$f | ✔ | ain_2__high__limit | 7510
Analogue Input 2 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7511 | FLOAT32 | 1 |  | 30 | 6506 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn2WrsL |  | mag | f | OS/GGIO1$MX$AnIn2WrsL$mag$f | ✔ | ain_2__low__limit | 7512
Analogue Input 2 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7513 | FLOAT32 | 1 |  | 30 | 6507 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn2AlsL |  | mag | f | OS/GGIO1$MX$AnIn2AlsL$mag$f | ✔ | ain_2__low_low__limit | 7514
Analogue Input 3 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7515 | FLOAT32 | 1 |  | 30 | 6508 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn3AlsH |  | mag | f | OS/GGIO1$MX$AnIn3AlsH$mag$f | ✔ | ain_3__high_high__limit | 7516
Analogue Input 3 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7517 | FLOAT32 | 1 |  | 30 | 6509 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn3WrsH |  | mag | f | OS/GGIO1$MX$AnIn3WrsH$mag$f | ✔ | ain_3__high__limit | 7518
Analogue Input 3 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7519 | FLOAT32 | 1 |  | 30 | 6510 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn3WrsL |  | mag | f | OS/GGIO1$MX$AnIn3WrsL$mag$f | ✔ | ain_3__low__limit | 7520
Analogue Input 3 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7521 | FLOAT32 | 1 |  | 30 | 6511 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn3AlsL |  | mag | f | OS/GGIO1$MX$AnIn3AlsL$mag$f | ✔ | ain_3__low_low__limit | 7522
Analogue Input 4 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7523 | FLOAT32 | 1 |  | 30 | 6512 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn4AlsH |  | mag | f | OS/GGIO1$MX$AnIn4AlsH$mag$f | ✔ | ain_4__high_high__limit | 7524
Analogue Input 4 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7525 | FLOAT32 | 1 |  | 30 | 6513 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn4WrsH |  | mag | f | OS/GGIO1$MX$AnIn4WrsH$mag$f | ✔ | ain_4__high__limit | 7526
Analogue Input 4 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7527 | FLOAT32 | 1 |  | 30 | 6514 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn4WrsL |  | mag | f | OS/GGIO1$MX$AnIn4WrsL$mag$f | ✔ | ain_4__low__limit | 7528
Analogue Input 4 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7529 | FLOAT32 | 1 |  | 30 | 6515 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn4AlsL |  | mag | f | OS/GGIO1$MX$AnIn4AlsL$mag$f | ✔ | ain_4__low_low__limit | 7530
Analogue Input 5 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7531 | FLOAT32 | 1 |  | 30 | 6516 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn5AlsH |  | mag | f | OS/GGIO1$MX$AnIn5AlsH$mag$f | ✔ | ain_5__high_high__limit | 7532
Analogue Input 5 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7533 | FLOAT32 | 1 |  | 30 | 6517 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn5WrsH |  | mag | f | OS/GGIO1$MX$AnIn5WrsH$mag$f | ✔ | ain_5__high__limit | 7534
Analogue Input 5 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7535 | FLOAT32 | 1 |  | 30 | 6518 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn5WrsL |  | mag | f | OS/GGIO1$MX$AnIn5WrsL$mag$f | ✔ | ain_5__low__limit | 7536
Analogue Input 5 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7537 | FLOAT32 | 1 |  | 30 | 6519 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn5AlsL |  | mag | f | OS/GGIO1$MX$AnIn5AlsL$mag$f | ✔ | ain_5__low_low__limit | 7538
Analogue Input 6 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7539 | FLOAT32 | 1 |  | 30 | 6520 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn6AlsH |  | mag | f | OS/GGIO1$MX$AnIn6AlsH$mag$f | ✔ | ain_6__high_high__limit | 7540
Analogue Input 6 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7541 | FLOAT32 | 1 |  | 30 | 6521 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn6WrsH |  | mag | f | OS/GGIO1$MX$AnIn6WrsH$mag$f | ✔ | ain_6__high__limit | 7542
Analogue Input 6 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7543 | FLOAT32 | 1 |  | 30 | 6522 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn6WrsL |  | mag | f | OS/GGIO1$MX$AnIn6WrsL$mag$f | ✔ | ain_6__low__limit | 7544
Analogue Input 6 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7545 | FLOAT32 | 1 |  | 30 | 6523 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn6AlsL |  | mag | f | OS/GGIO1$MX$AnIn6AlsL$mag$f | ✔ | ain_6__low_low__limit | 7546
Digital Input 1 Transition Total High-High Alarm Limit | General | 0 - 4,294,967,295 |  | 7547 | FLOAT32 | 1 |  | 30 | 6524 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr1AlsH |  | mag | f | OS/GGIO1$MX$DiTr1AlsH$mag$f | ✔ | din_1__transition_total__high_high__limit | 7548
Digital Input 1 Transition Total High Alarm Limit | General | 0 - 4,294,967,295 |  | 7549 | FLOAT32 | 1 |  | 30 | 6525 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr1WrsH |  | mag | f | OS/GGIO1$MX$DiTr1WrsH$mag$f | ✔ | din_1__transition_total__high__limit | 7550
Digital Input 2 Transition Total High-High Alarm Limit | General | 0 - 4,294,967,295 |  | 7551 | FLOAT32 | 1 |  | 30 | 6526 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr2AlsH |  | mag | f | OS/GGIO1$MX$DiTr2AlsH$mag$f | ✔ | din_2__transition_total__high_high__limit | 7552
Digital Input 2 Transition Total High Alarm Limit | General | 0 - 4,294,967,295 |  | 7553 | FLOAT32 | 1 |  | 30 | 6527 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr2WrsH |  | mag | f | OS/GGIO1$MX$DiTr2WrsH$mag$f | ✔ | din_2__transition_total__high__limit | 7554
Digital Input 3 Transition Total High-High Alarm Limit | General | 0 - 4,294,967,295 |  | 7555 | FLOAT32 | 1 |  | 30 | 6528 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr3AlsH |  | mag | f | OS/GGIO1$MX$DiTr3AlsH$mag$f | ✔ | din_3__transition_total__high_high__limit | 7556
Digital Input 3 Transition Total High Alarm Limit | General | 0 - 4,294,967,295 |  | 7557 | FLOAT32 | 1 |  | 30 | 6529 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr3WrsH |  | mag | f | OS/GGIO1$MX$DiTr3WrsH$mag$f | ✔ | din_3__transition_total__high__limit | 7558
Digital Input 4 Transition Total High-High Alarm Limit | General | 0 - 4,294,967,295 |  | 7559 | FLOAT32 | 1 |  | 30 | 6530 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr4AlsH |  | mag | f | OS/GGIO1$MX$DiTr4AlsH$mag$f | ✔ | din_4__transition_total__high_high__limit | 7560
Digital Input 4 Transition Total High Alarm Limit | General | 0 - 4,294,967,295 |  | 7561 | FLOAT32 | 1 |  | 30 | 6531 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr4WrsH |  | mag | f | OS/GGIO1$MX$DiTr4WrsH$mag$f | ✔ | din_4__transition_total__high__limit | 7562
Digital Input 5 Transition Total High-High Alarm Limit | General | 0 - 4,294,967,295 |  | 7563 | FLOAT32 | 1 |  | 30 | 6532 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr5AlsH |  | mag | f | OS/GGIO1$MX$DiTr5AlsH$mag$f | ✔ | din_5__transition_total__high_high__limit | 7564
Digital Input 5 Transition Total High Alarm Limit | General | 0 - 4,294,967,295 |  | 7565 | FLOAT32 | 1 |  | 30 | 6533 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr5WrsH |  | mag | f | OS/GGIO1$MX$DiTr5WrsH$mag$f | ✔ | din_5__transition_total__high__limit | 7566
Digital Input 6 Transition Total High-High Alarm Limit | General | 0 - 4,294,967,295 |  | 7567 | FLOAT32 | 1 |  | 30 | 6534 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr6AlsH |  | mag | f | OS/GGIO1$MX$DiTr6AlsH$mag$f | ✔ | din_6__transition_total__high_high__limit | 7568
Digital Input 6 Transition Total High Alarm Limit | General | 0 - 4,294,967,295 |  | 7569 | FLOAT32 | 1 |  | 30 | 6535 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr6WrsH |  | mag | f | OS/GGIO1$MX$DiTr6WrsH$mag$f | ✔ | din_6__transition_total__high__limit | 7570
Digital Input 7 Transition Total High-High Alarm Limit | General | 0 - 4,294,967,295 |  | 7571 | FLOAT32 | 1 |  | 30 | 6536 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr7AlsH |  | mag | f | OS/GGIO1$MX$DiTr7AlsH$mag$f | ✔ | din_7__transition_total__high_high__limit | 7572
Digital Input 7 Transition Total High Alarm Limit | General | 0 - 4,294,967,295 |  | 7573 | FLOAT32 | 1 |  | 30 | 6537 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr7WrsH |  | mag | f | OS/GGIO1$MX$DiTr7WrsH$mag$f | ✔ | din_7__transition_total__high__limit | 7574
Digital Input 8 Transition Total High-High Alarm Limit | General | 0 - 4,294,967,295 |  | 7575 | FLOAT32 | 1 |  | 30 | 6538 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr8AlsH |  | mag | f | OS/GGIO1$MX$DiTr8AlsH$mag$f | ✔ | din_8__transition_total__high_high__limit | 7576
Digital Input 8 Transition Total High Alarm Limit | General | 0 - 4,294,967,295 |  | 7577 | FLOAT32 | 1 |  | 30 | 6539 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr8WrsH |  | mag | f | OS/GGIO1$MX$DiTr8WrsH$mag$f | ✔ | din_8__transition_total__high__limit | 7578
Digital Input 9 Transition Total High-High Alarm Limit | General | 0 - 4,294,967,295 |  | 7579 | FLOAT32 | 1 |  | 30 | 6540 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr9AlsH |  | mag | f | OS/GGIO1$MX$DiTr9AlsH$mag$f | ✔ | din_9__transition_total__high_high__limit | 7580
Digital Input 9 Transition Total High Alarm Limit | General | 0 - 4,294,967,295 |  | 7581 | FLOAT32 | 1 |  | 30 | 6541 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | DiTr9WrsH |  | mag | f | OS/GGIO1$MX$DiTr9WrsH$mag$f | ✔ | din_9__transition_total__high__limit | 7582
Analogue Input 7 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7599 | FLOAT32 | 1 |  | 30 | 6600 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn7AlsH |  | mag | f | OS/GGIO1$MX$AnIn7AlsH$mag$f | ✔ | ain_7__high_high__limit | 7600
Analogue Input 7 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7601 | FLOAT32 | 1 |  | 30 | 6601 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn7WrsH |  | mag | f | OS/GGIO1$MX$AnIn7WrsH$mag$f | ✔ | ain_7__high__limit | 7602
Analogue Input 7 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7603 | FLOAT32 | 1 |  | 30 | 6602 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn7WrsL |  | mag | f | OS/GGIO1$MX$AnIn7WrsL$mag$f | ✔ | ain_7__low__limit | 7604
Analogue Input 7 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7605 | FLOAT32 | 1 |  | 30 | 6603 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn7AlsL |  | mag | f | OS/GGIO1$MX$AnIn7AlsL$mag$f | ✔ | ain_7__low_low__limit | 7606
Analogue Input 8 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7607 | FLOAT32 | 1 |  | 30 | 6604 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn8AlsH |  | mag | f | OS/GGIO1$MX$AnIn8AlsH$mag$f | ✔ | ain_8__high_high__limit | 7608
Analogue Input 8 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7609 | FLOAT32 | 1 |  | 30 | 6605 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn8WrsH |  | mag | f | OS/GGIO1$MX$AnIn8WrsH$mag$f | ✔ | ain_8__high__limit | 7610
Analogue Input 8 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7611 | FLOAT32 | 1 |  | 30 | 6606 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn8WrsL |  | mag | f | OS/GGIO1$MX$AnIn8WrsL$mag$f | ✔ | ain_8__low__limit | 7612
Analogue Input 8 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7613 | FLOAT32 | 1 |  | 30 | 6607 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn8AlsL |  | mag | f | OS/GGIO1$MX$AnIn8AlsL$mag$f | ✔ | ain_8__low_low__limit | 7614
Analogue Input 9 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7615 | FLOAT32 | 1 |  | 30 | 6608 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn9AlsH |  | mag | f | OS/GGIO1$MX$AnIn9AlsH$mag$f | ✔ | ain_9__high_high__limit | 7616
Analogue Input 9 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7617 | FLOAT32 | 1 |  | 30 | 6609 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn9WrsH |  | mag | f | OS/GGIO1$MX$AnIn9WrsH$mag$f | ✔ | ain_9__high__limit | 7618
Analogue Input 9 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7619 | FLOAT32 | 1 |  | 30 | 6610 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn9WrsL |  | mag | f | OS/GGIO1$MX$AnIn9WrsL$mag$f | ✔ | ain_9__low__limit | 7620
Analogue Input 9 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7621 | FLOAT32 | 1 |  | 30 | 6611 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn9AlsL |  | mag | f | OS/GGIO1$MX$AnIn9AlsL$mag$f | ✔ | ain_9__low_low__limit | 7622
Analogue Input 10 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7623 | FLOAT32 | 1 |  | 30 | 6612 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn10AlsH |  | mag | f | OS/GGIO1$MX$AnIn10AlsH$mag$f | ✔ | ain_10__high_high__limit | 7624
Analogue Input 10 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7625 | FLOAT32 | 1 |  | 30 | 6613 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn10WrsH |  | mag | f | OS/GGIO1$MX$AnIn10WrsH$mag$f | ✔ | ain_10__high__limit | 7626
Analogue Input 10 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7627 | FLOAT32 | 1 |  | 30 | 6614 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn10WrsL |  | mag | f | OS/GGIO1$MX$AnIn10WrsL$mag$f | ✔ | ain_10__low__limit | 7628
Analogue Input 10 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7629 | FLOAT32 | 1 |  | 30 | 6615 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn10AlsL |  | mag | f | OS/GGIO1$MX$AnIn10AlsL$mag$f | ✔ | ain_10__low_low__limit | 7630
Analogue Input 11 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7631 | FLOAT32 | 1 |  | 30 | 6616 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn11AlsH |  | mag | f | OS/GGIO1$MX$AnIn11AlsH$mag$f | ✔ | ain_11__high_high__limit | 7632
Analogue Input 11 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7633 | FLOAT32 | 1 |  | 30 | 6617 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn11WrsH |  | mag | f | OS/GGIO1$MX$AnIn11WrsH$mag$f | ✔ | ain_11__high__limit | 7634
Analogue Input 11 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7635 | FLOAT32 | 1 |  | 30 | 6618 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn11WrsL |  | mag | f | OS/GGIO1$MX$AnIn11WrsL$mag$f | ✔ | ain_11__low__limit | 7636
Analogue Input 11 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7637 | FLOAT32 | 1 |  | 30 | 6619 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn11AlsL |  | mag | f | OS/GGIO1$MX$AnIn11AlsL$mag$f | ✔ | ain_11__low_low__limit | 7638
Analogue Input 12 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7639 | FLOAT32 | 1 |  | 30 | 6620 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn12AlsH |  | mag | f | OS/GGIO1$MX$AnIn12AlsH$mag$f | ✔ | ain_12__high_high__limit | 7640
Analogue Input 12 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7641 | FLOAT32 | 1 |  | 30 | 6621 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn12WrsH |  | mag | f | OS/GGIO1$MX$AnIn12WrsH$mag$f | ✔ | ain_12__high__limit | 7642
Analogue Input 12 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7643 | FLOAT32 | 1 |  | 30 | 6622 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn12WrsL |  | mag | f | OS/GGIO1$MX$AnIn12WrsL$mag$f | ✔ | ain_12__low__limit | 7644
Analogue Input 12 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7645 | FLOAT32 | 1 |  | 30 | 6623 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn12AlsL |  | mag | f | OS/GGIO1$MX$AnIn12AlsL$mag$f | ✔ | ain_12__low_low__limit | 7646
Analogue Input 13 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7647 | FLOAT32 | 1 |  | 30 | 6624 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn13AlsH |  | mag | f | OS/GGIO1$MX$AnIn13AlsH$mag$f | ✔ | ain_13__high_high__limit | 7648
Analogue Input 13 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7649 | FLOAT32 | 1 |  | 30 | 6625 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn13WrsH |  | mag | f | OS/GGIO1$MX$AnIn13WrsH$mag$f | ✔ | ain_13__high__limit | 7650
Analogue Input 13 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7651 | FLOAT32 | 1 |  | 30 | 6626 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn13WrsL |  | mag | f | OS/GGIO1$MX$AnIn13WrsL$mag$f | ✔ | ain_13__low__limit | 7652
Analogue Input 13 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7653 | FLOAT32 | 1 |  | 30 | 6627 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn13AlsL |  | mag | f | OS/GGIO1$MX$AnIn13AlsL$mag$f | ✔ | ain_13__low_low__limit | 7654
Analogue Input 14 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7655 | FLOAT32 | 1 |  | 30 | 6628 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn14AlsH |  | mag | f | OS/GGIO1$MX$AnIn14AlsH$mag$f | ✔ | ain_14__high_high__limit | 7656
Analogue Input 14 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7657 | FLOAT32 | 1 |  | 30 | 6629 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn14WrsH |  | mag | f | OS/GGIO1$MX$AnIn14WrsH$mag$f | ✔ | ain_14__high__limit | 7658
Analogue Input 14 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7659 | FLOAT32 | 1 |  | 30 | 6630 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn14WrsL |  | mag | f | OS/GGIO1$MX$AnIn14WrsL$mag$f | ✔ | ain_14__low__limit | 7660
Analogue Input 14 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7661 | FLOAT32 | 1 |  | 30 | 6631 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn14AlsL |  | mag | f | OS/GGIO1$MX$AnIn14AlsL$mag$f | ✔ | ain_14__low_low__limit | 7662
Analogue Input 15 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7663 | FLOAT32 | 1 |  | 30 | 6632 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn15AlsH |  | mag | f | OS/GGIO1$MX$AnIn15AlsH$mag$f | ✔ | ain_15__high_high__limit | 7664
Analogue Input 15 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7665 | FLOAT32 | 1 |  | 30 | 6633 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn15WrsH |  | mag | f | OS/GGIO1$MX$AnIn15WrsH$mag$f | ✔ | ain_15__high__limit | 7666
Analogue Input 15 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7667 | FLOAT32 | 1 |  | 30 | 6634 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn15WrsL |  | mag | f | OS/GGIO1$MX$AnIn15WrsL$mag$f | ✔ | ain_15__low__limit | 7668
Analogue Input 15 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7669 | FLOAT32 | 1 |  | 30 | 6635 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn15AlsL |  | mag | f | OS/GGIO1$MX$AnIn15AlsL$mag$f | ✔ | ain_15__low_low__limit | 7670
Analogue Input 16 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7671 | FLOAT32 | 1 |  | 30 | 6636 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn16AlsH |  | mag | f | OS/GGIO1$MX$AnIn16AlsH$mag$f | ✔ | ain_16__high_high__limit | 7672
Analogue Input 16 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7673 | FLOAT32 | 1 |  | 30 | 6637 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn16WrsH |  | mag | f | OS/GGIO1$MX$AnIn16WrsH$mag$f | ✔ | ain_16__high__limit | 7674
Analogue Input 16 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7675 | FLOAT32 | 1 |  | 30 | 6638 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn16WrsL |  | mag | f | OS/GGIO1$MX$AnIn16WrsL$mag$f | ✔ | ain_16__low__limit | 7676
Analogue Input 16 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7677 | FLOAT32 | 1 |  | 30 | 6639 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn16AlsL |  | mag | f | OS/GGIO1$MX$AnIn16AlsL$mag$f | ✔ | ain_16__low_low__limit | 7678
Analogue Input 17 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7679 | FLOAT32 | 1 |  | 30 | 6640 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn17AlsH |  | mag | f | OS/GGIO1$MX$AnIn17AlsH$mag$f | ✔ | ain_17__high_high__limit | 7680
Analogue Input 17 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7681 | FLOAT32 | 1 |  | 30 | 6641 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn17WrsH |  | mag | f | OS/GGIO1$MX$AnIn17WrsH$mag$f | ✔ | ain_17__high__limit | 7682
Analogue Input 17 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7683 | FLOAT32 | 1 |  | 30 | 6642 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn17WrsL |  | mag | f | OS/GGIO1$MX$AnIn17WrsL$mag$f | ✔ | ain_17__low__limit | 7684
Analogue Input 17 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7685 | FLOAT32 | 1 |  | 30 | 6643 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn17AlsL |  | mag | f | OS/GGIO1$MX$AnIn17AlsL$mag$f | ✔ | ain_17__low_low__limit | 7686
Analogue Input 18 High-High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7687 | FLOAT32 | 1 |  | 30 | 6644 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn18AlsH |  | mag | f | OS/GGIO1$MX$AnIn18AlsH$mag$f | ✔ | ain_18__high_high__limit | 7688
Analogue Input 18 High Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7689 | FLOAT32 | 1 |  | 30 | 6645 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn18WrsH |  | mag | f | OS/GGIO1$MX$AnIn18WrsH$mag$f | ✔ | ain_18__high__limit | 7690
Analogue Input 18 Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7691 | FLOAT32 | 1 |  | 30 | 6646 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn18WrsL |  | mag | f | OS/GGIO1$MX$AnIn18WrsL$mag$f | ✔ | ain_18__low__limit | 7692
Analogue Input 18 Low-Low Alarm Limit (user defined) | General | -4,294,967,295 - 4,294,967,295 |  | 7693 | FLOAT32 | 1 |  | 30 | 6647 | 3 | 5 | 7 | ✔ | Disabled |  | OS | GGIO1 | MX | AnIn18AlsL |  | mag | f | OS/GGIO1$MX$AnIn18AlsL$mag$f | ✔ | ain_18__low_low__limit | 7694
System Date Time in Local Time in UNIX format | General | 0 - 4,294,967,295 s |  | 7999 | UINT32 | 1 |  | 30 | 7000 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn1 |  | stVal |  | OS/GGIO1$ST$IntIn1$stVal | ✔ | date_time_local | 8000
System Date Time in UTC in UNIX format | General | 0 - 4,294,967,295 s |  | 8001 | UINT32 | 1 |  | 30 | 7001 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn2 |  | stVal |  | OS/GGIO1$ST$IntIn2$stVal | ✔ | date_time | 8002
System Date in Local Time in GE binary format (see tab DNP3 Enumeration) | General | 0 - 4,294,967,295 |  | 8003 | DATE | 1 |  | 30 | 7002 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn3 |  | stVal |  | OS/GGIO1$ST$IntIn3$stVal | ✔ | date_local_ge | 8004
System Time in Local Time in GE binary format (see tab DNP3 Enumeration) | General | 0 - 4,294,967,295 |  | 8005 | TIME | 1 |  | 30 | 7003 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn4 |  | stVal |  | OS/GGIO1$ST$IntIn4$stVal | ✔ | time_local_ge | 8006
System Date in UTC in GE binary format (see tab DNP3 Enumeration) | General | 0 - 4,294,967,295 |  | 8007 | DATE | 1 |  | 30 | 7004 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn5 |  | stVal |  | OS/GGIO1$ST$IntIn5$stVal | ✔ | date_utc_ge | 8008
System Time in UTC in GE binary format (see tab DNP3 Enumeration) | General | 0 - 4,294,967,295 |  | 8009 | TIME | 1 |  | 30 | 7005 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn6 |  | stVal |  | OS/GGIO1$ST$IntIn6$stVal | ✔ | time_utc_ge | 8010
Source 1 Last DGA Measurement Date Time in Local Time in UNIX format | Source 1 | 0 - 4,294,967,295 s |  | 8011 | UINT32 | 1 |  | 30 | 7006 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn7 |  | stVal |  | OS/GGIO1$ST$IntIn7$stVal | ✔ | source_1__date_time_local | 8012
Source 1 Last DGA Measurement Date in Local Time in GE binary format (see tab DNP3 Enumeration) | Source 1 | 0 - 4,294,967,295 |  | 8013 | DATE | 1 |  | 30 | 7007 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn8 |  | stVal |  | OS/GGIO1$ST$IntIn8$stVal | ✔ | source_1__date_local_ge | 8014
Source 1 Last DGA Measurement Time in Local Time in GE binary format (see tab DNP3 Enumeration) | Source 1 | 0 - 4,294,967,295 |  | 8015 | TIME | 1 |  | 30 | 7008 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn9 |  | stVal |  | OS/GGIO1$ST$IntIn9$stVal | ✔ | source_1__time_local_ge | 8016
Source 1 Last DGA Measurement Date in UTC in GE binary format (see tab DNP3 Enumeration) | Source 1 | 0 - 4,294,967,295 |  | 8017 | DATE | 1 |  | 30 | 7009 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn10 |  | stVal |  | OS/GGIO1$ST$IntIn10$stVal | ✔ | source_1__date_utc_ge | 8018
Source 1 Last DGA Measurement Time in UTC in GE binary format (see tab DNP3 Enumeration) | Source 1 | 0 - 4,294,967,295 |  | 8019 | TIME | 1 |  | 30 | 7010 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn11 |  | stVal |  | OS/GGIO1$ST$IntIn11$stVal | ✔ | source_1__time_utc_ge | 8020
Source 1 Next DGA Measurement Date Time in Local Time in UNIX format | Source 1 | 0 - 4,294,967,295 s |  | 8021 | UINT32 | 1 |  | 30 | 7011 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn12 |  | stVal |  | OS/GGIO1$ST$IntIn12$stVal | ✔ | source_1__next_measurement_date_time_local | 8022
Source 1 Next DGA Measurement Date in Local Time in GE binary format (see tab DNP3 Enumeration) | Source 1 | 0 - 4,294,967,295 |  | 8023 | DATE | 1 |  | 30 | 7012 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn13 |  | stVal |  | OS/GGIO1$ST$IntIn13$stVal | ✔ | source_1__next_measurement_date_local_ge | 8024
Source 1 Next DGA Measurement Time in Local Time in GE binary format (see tab DNP3 Enumeration) | Source 1 | 0 - 4,294,967,295 |  | 8025 | TIME | 1 |  | 30 | 7013 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn14 |  | stVal |  | OS/GGIO1$ST$IntIn14$stVal | ✔ | source_1__next_measurement_time_local_ge | 8026
Source 1 Next DGA Measurement Date in UTC in GE binary format (see tab DNP3 Enumeration) | Source 1 | 0 - 4,294,967,295 |  | 8027 | DATE | 1 |  | 30 | 7014 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn15 |  | stVal |  | OS/GGIO1$ST$IntIn15$stVal | ✔ | source_1__next_measurement_date_utc_ge | 8028
Source 1 Next DGA Measurement Time in UTC in GE binary format (see tab DNP3 Enumeration) | Source 1 | 0 - 4,294,967,295 |  | 8029 | TIME | 1 |  | 30 | 7015 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn16 |  | stVal |  | OS/GGIO1$ST$IntIn16$stVal | ✔ | source_1__next_measurement_time_utc_ge | 8030
Source 1 DGA Scheduler Interval in Normal mode (seconds) | Source 1 | 0 - 4,294,967,295 s |  | 8031 | UINT32 | 1 |  | 30 | 7016 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn17 |  | stVal |  | OS/GGIO1$ST$IntIn17$stVal | ✔ | source_1__normal_interval | 8032
Source 1 DGA Scheduler Interval in Caution mode (seconds) | Source 1 | 0 - 4,294,967,295 s |  | 8033 | UINT32 | 1 |  | 30 | 7017 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn18 |  | stVal |  | OS/GGIO1$ST$IntIn18$stVal | ✔ | source_1__caution_interval | 8034
Source 1 DGA Scheduler Interval in Alarm mode (seconds) | Source 1 | 0 - 4,294,967,295 s |  | 8035 | UINT32 | 1 |  | 30 | 7018 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn19 |  | stVal |  | OS/GGIO1$ST$IntIn19$stVal | ✔ | source_1__alarm_interval | 8036
Source 1 PGA Error Codes (see tab DNP3 Enumeration) | Source 1 | 0 - 4,294,967,295 |  | 8037 | UINT32 | 1 |  | 30 | 7019 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn20 |  | stVal |  | OS/GGIO1$ST$IntIn20$stVal | ✔ | source_1__pga_error_codes | 8038
PreSens O2 Sensor Error Codes (Plus) | Source 1 | 0 - 4,294,967,295 |  | 8039 | UINT32 | 1 |  | 30 | 7020 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn21 |  | stVal |  | OS/GGIO1$ST$IntIn21$stVal | ✔ | source_1__presens_error_code | 8040
Source 1 Measurement Flags (see tab DNP3 Enumeration) | Source 1 | 0 - 4,294,967,295 |  | 8041 | UINT32 | 1 |  | 30 | 7021 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | IntIn22 |  | stVal |  | OS/GGIO1$ST$IntIn22$stVal | ✔ | source_1__measurement_flags | 8042
Host Firmware Version (see tab DNP3 Enumeration) | General | 0 - 4,294,967,295 |  | 8043 | UINT32 | 1 |  | 30 | 7022 | 2 | 1 | 3 | ✔ | Disabled |  | OS | GGIO1 | ST | IntIn23 |  | stVal |  | OS/GGIO1$ST$IntIn23$stVal | ✔ | mcb_firmware_version | 8044
Digital Input 1 Transition Total | General | 0 - 4,294,967,295 |  | 8499 | UINT32 | 1 |  | 30 | 7500 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | DiTr1 |  | stVal |  | OS/GGIO1$ST$DiTr1$stVal | ✔ | din_1__transition_total | 8500
Digital Input 2 Transition Total | General | 0 - 4,294,967,295 |  | 8501 | UINT32 | 1 |  | 30 | 7501 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | DiTr2 |  | stVal |  | OS/GGIO1$ST$DiTr2$stVal | ✔ | din_2__transition_total | 8502
Digital Input 3 Transition Total | General | 0 - 4,294,967,295 |  | 8503 | UINT32 | 1 |  | 30 | 7502 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | DiTr3 |  | stVal |  | OS/GGIO1$ST$DiTr3$stVal | ✔ | din_3__transition_total | 8504
Digital Input 4 Transition Total | General | 0 - 4,294,967,295 |  | 8505 | UINT32 | 1 |  | 30 | 7503 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | DiTr4 |  | stVal |  | OS/GGIO1$ST$DiTr4$stVal | ✔ | din_4__transition_total | 8506
Digital Input 5 Transition Total | General | 0 - 4,294,967,295 |  | 8507 | UINT32 | 1 |  | 30 | 7504 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | DiTr5 |  | stVal |  | OS/GGIO1$ST$DiTr5$stVal | ✔ | din_5__transition_total | 8508
Digital Input 6 Transition Total | General | 0 - 4,294,967,295 |  | 8509 | UINT32 | 1 |  | 30 | 7505 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | DiTr6 |  | stVal |  | OS/GGIO1$ST$DiTr6$stVal | ✔ | din_6__transition_total | 8510
Digital Input 7 Transition Total | General | 0 - 4,294,967,295 |  | 8511 | UINT32 | 1 |  | 30 | 7506 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | DiTr7 |  | stVal |  | OS/GGIO1$ST$DiTr7$stVal | ✔ | din_7__transition_total | 8512
Digital Input 8 Transition Total | General | 0 - 4,294,967,295 |  | 8513 | UINT32 | 1 |  | 30 | 7507 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | DiTr8 |  | stVal |  | OS/GGIO1$ST$DiTr8$stVal | ✔ | din_8__transition_total | 8514
Digital Input 9 Transition Total | General | 0 - 4,294,967,295 |  | 8515 | UINT32 | 1 |  | 30 | 7508 | 2 | 1 | 3 | ✔ | Active |  | OS | GGIO1 | ST | DiTr9 |  | stVal |  | OS/GGIO1$ST$DiTr9$stVal | ✔ | din_9__transition_total | 8516
Source 1 Current DGA Scheduler Mode (see tab DNP3 Enumeration) | Source 1 | 0-Normal, 1-Caution, 2-Alarm, 3-Suspended |  | 8998 | UINT16 | 1 |  | 30 | 7999 | 3 | 2 | 4 | ✔ | Active |  | OS | GGIO1 | ST | IntIn24 |  | stVal |  | OS/GGIO1$ST$IntIn24$stVal | ✔ | source_1__sched_mode | 8999
Source 1 H2 conc. (ppm) (Hydrogen) integer version | Source 1 | 0 - 65,535 |  | 8999 | UINT16 | 1 | [18 empty] | source_1__h2__integer_version | 9000
Source 1 CO2 conc. (ppm) (Carbon Dioxide) integer version | Source 1 | 0 - 65,535 |  | 9000 | UINT16 | 1 | [18 empty] | source_1__co2__integer_version | 9001
Source 1 CO conc. (ppm) (Carbon Monoxide) integer version | Source 1 | 0 - 65,535 |  | 9001 | UINT16 | 1 | [18 empty] | source_1__co__integer_version | 9002
Source 1 C2H4 conc. (ppm) (Ethylene) integer version | Source 1 | 0 - 65,535 |  | 9002 | UINT16 | 1 | [18 empty] | source_1__c2h4__integer_version | 9003
Source 1 C2H6 conc. (ppm) (Ethane) integer version | Source 1 | 0 - 65,535 |  | 9003 | UINT16 | 1 | [18 empty] | source_1__c2h6__integer_version | 9004
Source 1 CH4 conc. (ppm) (Methane) integer version | Source 1 | 0 - 65,535 |  | 9004 | UINT16 | 1 | [18 empty] | source_1__ch4__integer_version | 9005
Source 1 C2H2 conc. (ppm) (Acetylene) integer version | Source 1 | 0 - 65,535 |  | 9005 | UINT16 | 1 | [18 empty] | source_1__c2h2__integer_version | 9006
Source 1 H2O conc. (ppm) (Water) integer version | Source 1 | 0 - 65,535 |  | 9006 | UINT16 | 1 | [18 empty] | source_1__h2o__integer_version | 9007
Source 1 O2 conc. (ppm) (Oxygen) integer version | Source 1 | 0 - 65,535 |  | 9007 | UINT16 | 1 | [18 empty] | source_1__o2__integer_version | 9008
Source 1 TDCG conc. (ppm) (Total Dissolved Combustible Gases) integer version | Source 1 | 0 - 65,535 |  | 9008 | UINT16 | 10 | [18 empty] | source_1__tdcg__div10__integer_version | 9009
Source 1 TDCG conc. (ppm) (Total Dissolved Combustible Gases) integer version | Source 1 | 0 - 65,535 |  | 9009 | UINT16 | 1 | [18 empty] | source_1__tdcg__integer_version | 9010
Source 1 N2 conc. (ppm) (Nitrogen) integer version | Source 1 | 0 - 65,535 |  | 9010 | UINT16 | 10 | [18 empty] | source_1__n2__div10__integer_version | 9011
Source 1 N2 conc. (ppm) (Nitrogen) integer version | Source 1 | 0 - 65,535 |  | 9011 | UINT16 | 1 | [18 empty] | source_1__n2__integer_version | 9012
Source 1 TDG conc. (ppm) (Total Dissolved Gas) integer version | Source 1 | 0 - 65,535 |  | 9012 | UINT16 | 10 | [18 empty] | source_1__tdg__div10__integer_version | 9013
Source 1 TDG conc. (ppm) (Total Dissolved Gas) integer version | Source 1 | 0 - 65,535 |  | 9013 | UINT16 | 1 | [18 empty] | source_1__tdg__integer_version | 9014
Source 1 TDH conc. (ppm) (Total Dissolved Hydrocarbons) integer version | Source 1 | 0 - 65,535 |  | 9014 | UINT16 | 1 | [18 empty] | source_1__tdh__integer_version | 9015
Source 1 ESHL (%) (Estimated Safe Handling Limit) integer version | Source 1 | 0 - 65,535 |  | 9015 | UINT16 | 1 | [18 empty] | source_1__eshl__integer_version | 9016
Source 1 Oil Pressure (kPa) integer version | Source 1 | 0 - 65,535 |  | 9016 | UINT16 | 1 | [18 empty] | source_1__oil_pressure__integer_version | 9017
Source 1 RS (%) (Relative Saturation) integer version | Source 1 | 0 - 65,535 |  | 9017 | UINT16 | 1 | [18 empty] | source_1__relative_saturation__integer_version | 9018
PreSens O2 Sensor Error State (Plus) | Source 1 | 0 - 65,535 |  | 9018 | UINT16 | 1 |  | 30 | 8019 | 3 | 2 | 4 | ✔ | Active |  | OS | GGIO1 | ST | IntIn25 |  | stVal |  | OS/GGIO1$ST$IntIn25$stVal | ✔ | source_1__presens_error_state | 9019
Analogue Input 1 (user defined) integer version | General | -32,768 - 32,767 |  | 9199 | INT16 | 1 | [18 empty] | ain_1__integer_version | 9200
Analogue Input 2 (user defined) integer version | General | -32,768 - 32,767 |  | 9200 | INT16 | 1 | [18 empty] | ain_2__integer_version | 9201
Analogue Input 3 (user defined) integer version | General | -32,768 - 32,767 |  | 9201 | INT16 | 1 | [18 empty] | ain_3__integer_version | 9202
Analogue Input 4 (user defined) integer version | General | -32,768 - 32,767 |  | 9202 | INT16 | 1 | [18 empty] | ain_4__integer_version | 9203
Analogue Input 5 (user defined) integer version | General | -32,768 - 32,767 |  | 9203 | INT16 | 1 | [18 empty] | ain_5__integer_version | 9204
Analogue Input 6 (user defined) integer version | General | -32,768 - 32,767 |  | 9204 | INT16 | 1 | [18 empty] | ain_6__integer_version | 9205
Analogue Input 7 (user defined) integer version | General | -32,768 - 32,767 |  | 9205 | INT16 | 1 | [18 empty] | ain_7__integer_version | 9206
Analogue Input 8 (user defined) integer version | General | -32,768 - 32,767 |  | 9206 | INT16 | 1 | [18 empty] | ain_8__integer_version | 9207
Analogue Input 9 (user defined) integer version | General | -32,768 - 32,767 |  | 9207 | INT16 | 1 | [18 empty] | ain_9__integer_version | 9208
Analogue Input 10 (user defined) integer version | General | -32,768 - 32,767 |  | 9208 | INT16 | 1 | [18 empty] | ain_10__integer_version | 9209
Analogue Input 11 (user defined) integer version | General | -32,768 - 32,767 |  | 9209 | INT16 | 1 | [18 empty] | ain_11__integer_version | 9210
Analogue Input 12 (user defined) integer version | General | -32,768 - 32,767 |  | 9210 | INT16 | 1 | [18 empty] | ain_12__integer_version | 9211
Analogue Input 13 (user defined) integer version | General | -32,768 - 32,767 |  | 9211 | INT16 | 1 | [18 empty] | ain_13__integer_version | 9212
Analogue Input 14 (user defined) integer version | General | -32,768 - 32,767 |  | 9212 | INT16 | 1 | [18 empty] | ain_14__integer_version | 9213
Analogue Input 15 (user defined) integer version | General | -32,768 - 32,767 |  | 9213 | INT16 | 1 | [18 empty] | ain_15__integer_version | 9214
Analogue Input 16 (user defined) integer version | General | -32,768 - 32,767 |  | 9214 | INT16 | 1 | [18 empty] | ain_16__integer_version | 9215
Analogue Input 17 (user defined) integer version | General | -32,768 - 32,767 |  | 9215 | INT16 | 1 | [18 empty] | ain_17__integer_version | 9216
Analogue Input 18 (user defined) integer version | General | -32,768 - 32,767 |  | 9216 | INT16 | 1 | [18 empty] | ain_18__integer_version | 9217
TransOpto Channel 1 Temperature (°C) integer version | Trans Opto | -80 – 250 °C |  | 9499 | INT16 | 1 | [18 empty] | to_temperature_1__integer_version | 9500
TransOpto Channel 2 Temperature (°C) integer version | Trans Opto | -80 – 250 °C |  | 9500 | INT16 | 1 | [18 empty] | to_temperature_2__integer_version | 9501
TransOpto Channel 3 Temperature (°C) integer version | Trans Opto | -80 – 250 °C |  | 9501 | INT16 | 1 | [18 empty] | to_temperature_3__integer_version | 9502
TransOpto Channel 4 Temperature (°C) integer version | Trans Opto | -80 – 250 °C |  | 9502 | INT16 | 1 | [18 empty] | to_temperature_4__integer_version | 9503
TransOpto Channel 5 Temperature (°C) integer version | Trans Opto | -80 – 250 °C |  | 9503 | INT16 | 1 | [18 empty] | to_temperature_5__integer_version | 9504
TransOpto Channel 6 Temperature (°C) integer version | Trans Opto | -80 – 250 °C |  | 9504 | INT16 | 1 | [18 empty] | to_temperature_6__integer_version | 9505
TransOpto Channel 7 Temperature (°C) integer version | Trans Opto | -80 – 250 °C |  | 9505 | INT16 | 1 | [18 empty] | to_temperature_7__integer_version | 9506
TransOpto Channel 8 Temperature (°C) integer version | Trans Opto | -80 – 250 °C |  | 9506 | INT16 | 1 | [18 empty] | to_temperature_8__integer_version | 9507
Source 1 Oil Temperature (°C) integer version | Source 1 | -50 – 200 °C |  | 9799 | INT16 | 1 | [18 empty] | source_1__oil_temperature__integer_version | 9800
Source 1 Ambient Temperature (°C) integer version | Source 1 | -50 – 80 °C |  | 9800 | INT16 | 1 | [18 empty] | source_1__ambient_temperature__integer_version | 9801
Source 1 Normalization Temperature (°C) integer version | Source 1 | 0 – 20 °C |  | 9801 | INT16 | 1 | [18 empty] | source_1__norm_temperature__integer_version | 9802
Source 1 PGA Error State | Source 1 | -32,768 - 32,767 |  | 9802 | INT16 | 1 |  | 30 | 8803 | 2 | 2 | 4 | ✔ | Active |  | OS | GGIO1 | ST | IntIn26 |  | stVal |  | OS/GGIO1$ST$IntIn26$stVal | ✔ | source_1__pga_error_state | 9803
MCB System ID (characters 1-2) | General | N/A |  | 9899 | TEXT | N/A |  | 30 | 8900 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_product_id (characters 1-2) | 9900
MCB System ID (characters 3-4) | General | N/A |  | 9900 | TEXT | N/A |  | 30 | 8901 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_product_id (characters 3-4) | 9901
MCB System ID (characters 5-6) | General | N/A |  | 9901 | TEXT | N/A |  | 30 | 8902 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_product_id (characters 5-6) | 9902
MCB System ID (characters 7-8) | General | N/A |  | 9902 | TEXT | N/A |  | 30 | 8903 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_product_id (characters 7-8) | 9903
MCB System ID (characters 9-10) | General | N/A |  | 9903 | TEXT | N/A |  | 30 | 8904 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_product_id (characters 9-10) | 9904
MCB System ID (characters 11-12) | General | N/A |  | 9904 | TEXT | N/A |  | 30 | 8905 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_product_id (characters 11-12) | 9905
MCB System ID (characters 13-14) | General | N/A |  | 9905 | TEXT | N/A |  | 30 | 8906 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_product_id (characters 13-14) | 9906
MCB System ID (characters 15-16) | General | N/A |  | 9906 | TEXT | N/A |  | 30 | 8907 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_product_id (characters 15-16) | 9907
MCB System ID (characters 17-18) | General | N/A |  | 9907 | TEXT | N/A |  | 30 | 8908 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_product_id (characters 17-18) | 9908
MCB System ID (characters 19-20) | General | N/A |  | 9908 | TEXT | N/A |  | 30 | 8909 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_product_id (characters 19-20) | 9909
MCB System ID (characters 21-22) | General | N/A |  | 9909 | TEXT | N/A |  | 30 | 8910 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_product_id (characters 21-22) | 9910
MCB System ID (characters 23-24) | General | N/A |  | 9910 | TEXT | N/A |  | 30 | 8911 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_product_id (characters 23-24) | 9911
MCB System ID (characters 25-26) | General | N/A |  | 9911 | TEXT | N/A |  | 30 | 8912 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_product_id (characters 25-26) | 9912
MCB System ID (characters 27-28) | General | N/A |  | 9912 | TEXT | N/A |  | 30 | 8913 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_product_id (characters 27-28) | 9913
MCB System ID (characters 29-30) | General | N/A |  | 9913 | TEXT | N/A |  | 30 | 8914 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_product_id (characters 29-30) | 9914
MCB System ID (characters 31-32) | General | N/A |  | 9914 | TEXT | N/A |  | 30 | 8915 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_product_id (characters 31-32) | 9915
MCB 900 Serial Number (characters 1-2) | General | N/A |  | 9915 | TEXT | N/A |  | 30 | 8916 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_serial_number (characters 1-2) | 9916
MCB 900 Serial Number (characters 3-4) | General | N/A |  | 9916 | TEXT | N/A |  | 30 | 8917 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_serial_number (characters 3-4) | 9917
MCB 900 Serial Number (characters 5-6) | General | N/A |  | 9917 | TEXT | N/A |  | 30 | 8918 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_serial_number (characters 5-6) | 9918
MCB 900 Serial Number (characters 7-8) | General | N/A |  | 9918 | TEXT | N/A |  | 30 | 8919 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_serial_number (characters 7-8) | 9919
MCB 900 Serial Number (characters 9-10) | General | N/A |  | 9919 | TEXT | N/A |  | 30 | 8920 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_serial_number (characters 9-10) | 9920
MCB 900 Serial Number (characters 11-12) | General | N/A |  | 9920 | TEXT | N/A |  | 30 | 8921 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_serial_number (characters 11-12) | 9921
MCB 900 Serial Number (characters 13-14) | General | N/A |  | 9921 | TEXT | N/A |  | 30 | 8922 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_serial_number (characters 13-14) | 9922
MCB 900 Serial Number (characters 15-16) | General | N/A |  | 9922 | TEXT | N/A |  | 30 | 8923 | 3 | 4 | 2 | ✔ | Active | [10 empty] | mcb_serial_number (characters 15-16) | 9923
TH Apparent Power in Winding H (MVA) | Models | 0 – 10000 |  | 9999 | FLOAT32 | 1 |  | 30 | 12000 | 2 | 5 | 7 | ✔ | Disabled |  | MO | MMXU1 | MX | VA | phsA | mag | f | MO/MMXU1$MX$VA$phsA$mag$f | ✔ | mo_mva_apparent_power_h | 10000
TH Apparent Power in Winding X (MVA) | Models | 0 – 10000 |  | 10001 | FLOAT32 | 1 |  | 30 | 12001 | 2 | 5 | 7 | ✔ | Disabled |  | MO | MMXU1 | MX | VA | phsB | mag | f | MO/MMXU1$MX$VA$phsB$mag$f | ✔ | mo_mva_apparent_power_x | 10002
TH Apparent Power in Winding Y (MVA) | Models | 0 – 10000 |  | 10003 | FLOAT32 | 1 |  | 30 | 12002 | 2 | 5 | 7 | ✔ | Disabled |  | MO | MMXU1 | MX | VA | phsC | mag | f | MO/MMXU1$MX$VA$phsC$mag$f | ✔ | mo_mva_apparent_power_y | 10004
TH Max Apparent Power in Winding H since last recording (MVA) | Models | 0 – 10000 |  | 10005 | FLOAT32 | 1 |  | 30 | 12003 | 2 | 5 | 7 | ✔ | Disabled |  | MO | MMXU1 | MX | MaxVA | phsA | mag | f | MO/MMXU1$MX$MaxVA$phsA$mag$f | ✔ | mo_mva_max_apparent_power_h | 10006
TH Max Apparent Power in Winding X since last recording (MVA) | Models | 0 – 10000 |  | 10007 | FLOAT32 | 1 |  | 30 | 12004 | 2 | 5 | 7 | ✔ | Disabled |  | MO | MMXU1 | MX | MaxVA | phsB | mag | f | MO/MMXU1$MX$MaxVA$phsB$mag$f | ✔ | mo_mva_max_apparent_power_x | 10008
TH Max Apparent Power in Winding Y since last recording (MVA) | Models | 0 – 10000 |  | 10009 | FLOAT32 | 1 |  | 30 | 12005 | 2 | 5 | 7 | ✔ | Disabled |  | MO | MMXU1 | MX | MaxVA | phsC | mag | f | MO/MMXU1$MX$MaxVA$phsC$mag$f | ✔ | mo_mva_max_apparent_power_y | 10010
TH Hot Spot Temp n Winding H (°C) | Models | -50 – 300 |  | 10011 | FLOAT32 | 1 |  | 30 | 12006 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | HPTmpClc1 |  | mag | f | MO/SPTR1$MX$HPTmpClc1$mag$f | ✔ | mo_whst_hot_spot_temp_h | 10012
TH Hot Spot Temp n Winding X (°C) | Models | -50 – 300 |  | 10013 | FLOAT32 | 1 |  | 30 | 12007 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | HPTmpClc2 |  | mag | f | MO/SPTR1$MX$HPTmpClc2$mag$f | ✔ | mo_whst_hot_spot_temp_x | 10014
TH Hot Spot Temp n Winding Y (°C) | Models | -50 – 300 |  | 10015 | FLOAT32 | 1 |  | 30 | 12008 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | HPTmpClc3 |  | mag | f | MO/SPTR1$MX$HPTmpClc3$mag$f | ✔ | mo_whst_hot_spot_temp_y | 10016
TH Winding Hottest Hot Spot Temperature (°C) | Models | -50 – 300 |  | 10017 | FLOAT32 | 1 |  | 30 | 12009 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | HPTmpMax |  | mag | f | MO/SPTR1$MX$HPTmpMax$mag$f | ✔ | mo_whst_winding_hottest_hot_spot_temperature | 10018
TH Deviation of current in Winding H (%) | Models | -100 – 100 |  | 10019 | FLOAT32 | 1 |  | 30 | 12010 | 2 | 5 | 7 | ✔ | Disabled |  | MO | MMXU1 | MX | ImbA | phsA | mag | f | MO/MMXU1$MX$ImbA$phsA$mag$f | ✔ | mo_whst_dev_current_a | 10020
TH Deviation of current in Winding X (%) | Models | -100 – 100 |  | 10021 | FLOAT32 | 1 |  | 30 | 12011 | 2 | 5 | 7 | ✔ | Disabled |  | MO | MMXU1 | MX | ImbA | phsB | mag | f | MO/MMXU1$MX$ImbA$phsB$mag$f | ✔ | mo_whst_dev_current_b | 10022
TH Deviation of current in Winding Y (%) | Models | -100 – 100 |  | 10023 | FLOAT32 | 1 |  | 30 | 12012 | 2 | 5 | 7 | ✔ | Disabled |  | MO | MMXU1 | MX | ImbA | phsC | mag | f | MO/MMXU1$MX$ImbA$phsC$mag$f | ✔ | mo_whst_dev_current_c | 10024
TH Average Phase Current (Amp) | Models | 0 – 10000 |  | 10025 | FLOAT32 | 1 |  | 30 | 12013 | 2 | 5 | 7 | ✔ | Disabled |  | MO | MMXU1 | MX | ImbAvg |  | mag | f | MO/MMXU1$MX$ImbAvg$mag$f | ✔ | mo_whst_dev_avr_current | 10026
TH Relative saturation at a standard temperature (%) | Models | 0 – 100 |  | 10027 | FLOAT32 | 1 |  | 30 | 12014 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | Mst |  | mag | f | MO/SPTR1$MX$Mst$mag$f | ✔ | mo_mco_relative_saturation | 10028
TH Temperature of Water condensation in oil (°C) | Models | -300 – 200 |  | 10029 | FLOAT32 | 1 |  | 30 | 12015 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | CdsTmp |  | mag | f | MO/SPTR1$MX$CdsTmp$mag$f | ✔ | mo_mco_water_cond_temp | 10030
TH Moisture Content in Winding Paper (%) | Models | 0 – 100 |  | 10031 | FLOAT32 | 1 |  | 30 | 12016 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | MstPap |  | mag | f | MO/SPTR1$MX$MstPap$mag$f | ✔ | mo_mstwind_moisture_in_paper | 10032
TH Bubbling Temperature (°C) | Models | -50 – 300 |  | 10033 | FLOAT32 | 1 |  | 30 | 12017 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | BubTmp |  | mag | f | MO/SPTR1$MX$BubTmp$mag$f | ✔ | mo_mstwind_bubbling_temperature | 10034
TH Bubbling Temperature Margin (°C) | Models | -50 – 300 |  | 10035 | FLOAT32 | 1 |  | 30 | 12018 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | BubTmpMar |  | mag | f | MO/SPTR1$MX$BubTmpMar$mag$f | ✔ | mo_mstwind_bubbling_temperature_margin | 10036
TH Remaining Time until Winding Insulation model Reliable (day) | Models | 0 – 1000 |  | 10037 | FLOAT32 | 1 |  | 30 | 12019 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | InsTmms1 |  | mag | f | MO/SPTR1$MX$InsTmms1$mag$f | ✔ | mo_mstwind_remaining_time_until_reliable | 10038
TH Moisture Content in Pressboard Barrier (%) | Models | 0 – 100 |  | 10039 | FLOAT32 | 1 |  | 30 | 12020 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | MstBar |  | mag | f | MO/SPTR1$MX$MstBar$mag$f | ✔ | mo_mstinsbar_moisture_insulation_barrier | 10040
TH Thermal aging acceleration factor | Models | 0 – 100 |  | 10041 | FLOAT32 | 1 |  | 30 | 12021 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | AgeRte1 |  | mag | f | MO/SPTR1$MX$AgeRte1$mag$f | ✔ | mo_iam_thermal_aging_acceleration_factor | 10042
TH Moisture aging acceleration factor | Models | 0 – 20 |  | 10043 | FLOAT32 | 1 |  | 30 | 12022 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | AgeRte2 |  | mag | f | MO/SPTR1$MX$AgeRte2$mag$f | ✔ | mo_iam_moisture_aging_acceleration_factor | 10044
TH Oxygen aging acceleration factor | Models | 0 – 20 |  | 10045 | FLOAT32 | 1 |  | 30 | 12023 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | AgeRte3 |  | mag | f | MO/SPTR1$MX$AgeRte3$mag$f | ✔ | mo_iam_oxygen_aging_acceleration_factor | 10046
TH Global aging acceleration factor | Models | 0.001 – 100 |  | 10047 | FLOAT32 | 1 |  | 30 | 12024 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | AgeRte4 |  | mag | f | MO/SPTR1$MX$AgeRte4$mag$f | ✔ | mo_iam_global_aging_acceleration_factor | 10048
Overload value of the Overload factor for for K (p.u.) = 1.1 in units of the Factor (see Section 3). | Models | 0 - 4,294,967,295 |  | 10049 | FLOAT32 | 1 |  | 30 | 12025 | 2 | 5 | 7 | ✔ | Disabled |  | MO | YPTR1 | MX | OvlVal1 |  | mag | f | MO/YPTR1$MX$OvlVal1$mag$f | ✔ | mo_dlg_overload_value_11 | 10050
Overload value of the Overload factor for for K (p.u.) = 1.2 in units of the Factor (see Section 3). | Models | 0 - 4,294,967,295 |  | 10051 | FLOAT32 | 1 |  | 30 | 12026 | 2 | 5 | 7 | ✔ | Disabled |  | MO | YPTR1 | MX | OvlVal2 |  | mag | f | MO/YPTR1$MX$OvlVal2$mag$f | ✔ | mo_dlg_overload_value_12 | 10052
Overload value of the Overload factor for for K (p.u.) = 1.3 in units of the Factor (see Section 3). | Models | 0 - 4,294,967,295 |  | 10053 | FLOAT32 | 1 |  | 30 | 12027 | 2 | 5 | 7 | ✔ | Disabled |  | MO | YPTR1 | MX | OvlVal3 |  | mag | f | MO/YPTR1$MX$OvlVal3$mag$f | ✔ | mo_dlg_overload_value_13 | 10054
Overload value of the Overload factor for for K (p.u.) = 1.4 in units of the Factor (see Section 3). | Models | 0 - 4,294,967,295 |  | 10055 | FLOAT32 | 1 |  | 30 | 12028 | 2 | 5 | 7 | ✔ | Disabled |  | MO | YPTR1 | MX | OvlVal4 |  | mag | f | MO/YPTR1$MX$OvlVal4$mag$f | ✔ | mo_dlg_overload_value_14 | 10056
Overload value of the Overload factor for for K (p.u.) = 1.5 in units of the Factor (see Section 3). | Models | 0 - 4,294,967,295 |  | 10057 | FLOAT32 | 1 |  | 30 | 12029 | 2 | 5 | 7 | ✔ | Disabled |  | MO | YPTR1 | MX | OvlVal5 |  | mag | f | MO/YPTR1$MX$OvlVal5$mag$f | ✔ | mo_dlg_overload_value_15 | 10058
Overload value of the Overload factor for for K (p.u.) = 1.6 in units of the Factor (see Section 3). | Models | 0 - 4,294,967,295 |  | 10059 | FLOAT32 | 1 |  | 30 | 12030 | 2 | 5 | 7 | ✔ | Disabled |  | MO | YPTR1 | MX | OvlVal6 |  | mag | f | MO/YPTR1$MX$OvlVal6$mag$f | ✔ | mo_dlg_overload_value_16 | 10060
Overload value of the Overload factor for for K (p.u.) = 1.7 in units of the Factor (see Section 3). | Models | 0 - 4,294,967,295 |  | 10061 | FLOAT32 | 1 |  | 30 | 12031 | 2 | 5 | 7 | ✔ | Disabled |  | MO | YPTR1 | MX | OvlVal7 |  | mag | f | MO/YPTR1$MX$OvlVal7$mag$f | ✔ | mo_dlg_overload_value_17 | 10062
Overload value of the Overload factor for for K (p.u.) = 1.8 in units of the Factor (see Section 3). | Models | 0 - 4,294,967,295 |  | 10063 | FLOAT32 | 1 |  | 30 | 12032 | 2 | 5 | 7 | ✔ | Disabled |  | MO | YPTR1 | MX | OvlVal8 |  | mag | f | MO/YPTR1$MX$OvlVal8$mag$f | ✔ | mo_dlg_overload_value_18 | 10064
Overload value of the Overload factor for for K (p.u.) = 1.9 in units of the Factor (see Section 3). | Models | 0 - 4,294,967,295 |  | 10065 | FLOAT32 | 1 |  | 30 | 12033 | 2 | 5 | 7 | ✔ | Disabled |  | MO | YPTR1 | MX | OvlVal9 |  | mag | f | MO/YPTR1$MX$OvlVal9$mag$f | ✔ | mo_dlg_overload_value_19 | 10066
Overload value of the Overload factor for for K (p.u.) = 2.0 in units of the Factor (see Section 3). | Models | 0 - 4,294,967,295 |  | 10067 | FLOAT32 | 1 |  | 30 | 12034 | 2 | 5 | 7 | ✔ | Disabled |  | MO | YPTR1 | MX | OvlVal10 |  | mag | f | MO/YPTR1$MX$OvlVal10$mag$f | ✔ | mo_dlg_overload_value_20 | 10068
Temperature difference averaged for Cooling Efficiency (°C) | Models | 0 - 4,294,967,295 |  | 10069 | FLOAT32 | 1 |  | 30 | 12035 | 2 | 5 | 7 | ✔ | Disabled |  | MO | GGIO4 | MX | AnIn1 |  | mag | f | MO/GGIO4$MX$AnIn1$mag$f | ✔ | mo_cem_temp_diff_avr | 10070
OLTC Short Term Difference in Oil Temperature main tank-OLTC (°C) | Models | -50 – 150 |  | 10071 | FLOAT32 | 1 |  | 30 | 12036 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | Tmp1 |  | mag | f | MO/SLTC1$MX$Tmp1$mag$f | ✔ | mo_oltc_temp_oil_short_term_diff | 10072
OLTC Long Term Difference in Oil Temperatur main tank-OLTCe (°C) | Models | -50 – 150 |  | 10073 | FLOAT32 | 1 |  | 30 | 12037 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | Tmp2 |  | mag | f | MO/SLTC1$MX$Tmp2$mag$f | ✔ | mo_oltc_temp_oil_long_term_diff | 10074
OLTC Motor Torque Total Time (sec) | Models | 0 - 4,294,967,295 |  | 10075 | FLOAT32 | 1 |  | 30 | 12038 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | TorqTm1 |  | mag | f | MO/SLTC1$MX$TorqTm1$mag$f | ✔ | mo_oltc_torque_total_time | 10076
OLTC Motor Torque In-Rush Time (sec) | Models | 0 - 4,294,967,295 |  | 10077 | FLOAT32 | 1 |  | 30 | 12039 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | TorqTm2 |  | mag | f | MO/SLTC1$MX$TorqTm2$mag$f | ✔ | mo_oltc_torque_inrush_time | 10078
OLTC Motor Torque Maximum 1 (W) | Models | 0 - 4,294,967,295 |  | 10079 | FLOAT32 | 1 |  | 30 | 12040 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | Torq1 |  | mag | f | MO/SLTC1$MX$Torq1$mag$f | ✔ | mo_oltc_torque_max_pwr1 | 10080
OLTC Motor Torque Maximum 2 (W) | Models | 0 - 4,294,967,295 |  | 10081 | FLOAT32 | 1 |  | 30 | 12041 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | Torq2 |  | mag | f | MO/SLTC1$MX$Torq2$mag$f | ✔ | mo_oltc_torque_max_pwr2 | 10082
OLTC Motor Torque Maximum 3 (W) | Models | 0 - 4,294,967,295 |  | 10083 | FLOAT32 | 1 |  | 30 | 12042 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | Torq3 |  | mag | f | MO/SLTC1$MX$Torq3$mag$f | ✔ | mo_oltc_torque_max_pwr3 | 10084
OLTC Motor Average Torque (W) | Models | 0 - 4,294,967,295 |  | 10085 | FLOAT32 | 1 |  | 30 | 12043 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | TorqAvg |  | mag | f | MO/SLTC1$MX$TorqAvg$mag$f | ✔ | mo_oltc_torque_avg_pwr | 10086
OLTC Motor Torque Total Time (%) | Models | 0 - 4,294,967,295 |  | 10087 | FLOAT32 | 1 |  | 30 | 12044 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | TorqTmPct1 |  | mag | f | MO/SLTC1$MX$TorqTmPct1$mag$f | ✔ | mo_oltc_torque_total_time_pct | 10088
OLTC Motor Torque In-Rush Time (%) | Models | 0 - 4,294,967,295 |  | 10089 | FLOAT32 | 1 |  | 30 | 12045 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | TorqTmPct2 |  | mag | f | MO/SLTC1$MX$TorqTmPct2$mag$f | ✔ | mo_oltc_torque_inrush_time_pct | 10090
OLTC Motor Torque Maximum 1 (%) | Models | 0 - 4,294,967,295 |  | 10091 | FLOAT32 | 1 |  | 30 | 12046 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | TorqPct1 |  | mag | f | MO/SLTC1$MX$TorqPct1$mag$f | ✔ | mo_oltc_torque_max_pwr1_pct | 10092
OLTC Motor Torque Maximum 2 (%) | Models | 0 - 4,294,967,295 |  | 10093 | FLOAT32 | 1 |  | 30 | 12047 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | TorqPct2 |  | mag | f | MO/SLTC1$MX$TorqPct2$mag$f | ✔ | mo_oltc_torque_max_pwr2_pct | 10094
OLTC Motor Torque Maximum 3 (%) | Models | 0 - 4,294,967,295 |  | 10095 | FLOAT32 | 1 |  | 30 | 12048 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | TorqPct3 |  | mag | f | MO/SLTC1$MX$TorqPct3$mag$f | ✔ | mo_oltc_torque_max_pwr3_pct | 10096
OLTC Motor Average Torque (%) | Models | 0 - 4,294,967,295 |  | 10097 | FLOAT32 | 1 |  | 30 | 12049 | 2 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | TorqPctAvg |  | mag | f | MO/SLTC1$MX$TorqPctAvg$mag$f | ✔ | mo_oltc_torque_avg_pwr_pct | 10098
TH Winding Hottest Hot Spot Temperature (°C) High-High Alarm limit | Models | 50 – 250 |  | 10199 | FLOAT32 | 1 |  | 30 | 12200 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | HPTmpAls |  | mag | f | MO/SPTR1$MX$HPTmpAls$mag$f | ✔ | mo_whst_winding_hottest_hot_spot_temperature__high_high__limit | 10200
TH Winding Hottest Hot Spot Temperature (°C) High Alarm Limit | Models | 50 – 250 |  | 10201 | FLOAT32 | 1 |  | 30 | 12201 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | HPTmpWrs |  | mag | f | MO/SPTR1$MX$HPTmpWrs$mag$f | ✔ | mo_whst_winding_hottest_hot_spot_temperature__high__limit | 10202
TH Temperature of Water condensation in oil (°C) High-High Alarm Limit | Models | -40 – 20 |  | 10203 | FLOAT32 | 1 |  | 30 | 12202 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | CdsTmpAls |  | mag | f | MO/SPTR1$MX$CdsTmpAls$mag$f | ✔ | mo_mco_water_cond_temp__high_high__limit | 10204
TH Temperature of Water condensation in oil (°C) High Alarm Limit | Models | -40 – 20 |  | 10205 | FLOAT32 | 1 |  | 30 | 12203 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | CdsTmpWrs |  | mag | f | MO/SPTR1$MX$CdsTmpWrs$mag$f | ✔ | mo_mco_water_cond_temp__high__limit | 10206
TH Bubbling Temperature Margin (°C) Low Alarm Limit | Models | 0 – 50 |  | 10207 | FLOAT32 | 1 |  | 30 | 12204 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | BubTmpAls |  | mag | f | MO/SPTR1$MX$BubTmpAls$mag$f | ✔ | mo_mstwind_bubbling_temperature_margin__low__limit | 10208
TH Bubbling Temperature Margin (°C) Low-Low Alarm Limit | Models | 0 – 50 |  | 10209 | FLOAT32 | 1 |  | 30 | 12205 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | BubTmpWrs |  | mag | f | MO/SPTR1$MX$BubTmpWrs$mag$f | ✔ | mo_mstwind_bubbling_temperature_margin__low_low__limit | 10210
TH Moisture Content in Pressboard Barrier (%) High-High Alarm Limit | Models | 0.5 – 10 |  | 10211 | FLOAT32 | 1 |  | 30 | 12206 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | MstAls |  | mag | f | MO/SPTR1$MX$MstAls$mag$f | ✔ | mo_mstinsbar_moisture_insulation_barrier__high_high__limit | 10212
TH Moisture Content in Pressboard Barrier (%) High Alarm Limit | Models | 0.5 – 10 |  | 10213 | FLOAT32 | 1 |  | 30 | 12207 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SPTR1 | MX | MstWrs |  | mag | f | MO/SPTR1$MX$MstWrs$mag$f | ✔ | mo_mstinsbar_moisture_insulation_barrier__high__limit | 10214
COOL Cooling bank 1 Continuous non-operational time (Hours) High Alarm Limit | Models | 100 – 10000 |  | 10215 | FLOAT32 | 1 |  | 30 | 12208 | 3 | 5 | 7 | ✔ | Disabled |  | MO | GGIO4 | MX | AnIn2 |  | mag | f | MO/GGIO4$MX$AnIn2$mag$f | ✔ | mo_csm_cooling_bank_1_continuous_nonoperational_time_hour__high__limit | 10216
COOL Cooling bank 2 Continuous non-operational time (Hours) High Alarm Limit | Models | 100 – 10000 |  | 10217 | FLOAT32 | 1 |  | 30 | 12209 | 3 | 5 | 7 | ✔ | Disabled |  | MO | GGIO4 | MX | AnIn3 |  | mag | f | MO/GGIO4$MX$AnIn3$mag$f | ✔ | mo_csm_cooling_bank_2_continuous_nonoperational_time_hour__high__limit | 10218
COOL Cooling bank 3 Continuous non-operational time (Hours) High Alarm Limit | Models | 100 – 10000 |  | 10219 | FLOAT32 | 1 |  | 30 | 12210 | 3 | 5 | 7 | ✔ | Disabled |  | MO | GGIO4 | MX | AnIn4 |  | mag | f | MO/GGIO4$MX$AnIn4$mag$f | ✔ | mo_csm_cooling_bank_3_continuous_nonoperational_time_hour__high__limit | 10220
COOL Cooling bank 4 Continuous non-operational time (Hours) High Alarm Limit | Models | 100 – 10000 |  | 10221 | FLOAT32 | 1 |  | 30 | 12211 | 3 | 5 | 7 | ✔ | Disabled |  | MO | GGIO4 | MX | AnIn5 |  | mag | f | MO/GGIO4$MX$AnIn5$mag$f | ✔ | mo_csm_cooling_bank_4_continuous_nonoperational_time_hour__high__limit | 10222
COOL Cooling efficiency - Temperature difference (°C) High-High Alarm Limit | Models | 5 – 50 |  | 10223 | FLOAT32 | 1 |  | 30 | 12212 | 3 | 5 | 7 | ✔ | Disabled |  | MO | GGIO4 | MX | AnIn6 |  | mag | f | MO/GGIO4$MX$AnIn6$mag$f | ✔ | mo_cem_temp_diff_avr__high_high__limit | 10224
COOL Cooling efficiency - Temperature difference (°C) High Alarm Limit | Models | 5 – 50 |  | 10225 | FLOAT32 | 1 |  | 30 | 12213 | 3 | 5 | 7 | ✔ | Disabled |  | MO | GGIO4 | MX | AnIn7 |  | mag | f | MO/GGIO4$MX$AnIn7$mag$f | ✔ | mo_cem_temp_diff_avr__high__limit | 10226
OLTC Short Term Difference in Oil Temperature main tank-OLTC (°C) High-High Alarm Limit | Models | 0 – 40 |  | 10227 | FLOAT32 | 1 |  | 30 | 12214 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | Tmp1Als |  | mag | f | MO/SLTC1$MX$Tmp1Als$mag$f | ✔ | mo_oltc_temp_oil_short_term_diff__high_high__limit | 10228
OLTC Short Term Difference in Oil Temperature main tank-OLTC (°C) High Alarm Limit | Models | 0 – 30 |  | 10229 | FLOAT32 | 1 |  | 30 | 12215 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | Tmp1Wrs |  | mag | f | MO/SLTC1$MX$Tmp1Wrs$mag$f | ✔ | mo_oltc_temp_oil_short_term_diff__high__limit | 10230
OLTC Long Term Difference in Oil Temperature main tank-OLTC (°C) High-High Alarm Limit | Models | 0 – 30 |  | 10231 | FLOAT32 | 1 |  | 30 | 12216 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | Tmp2Als |  | mag | f | MO/SLTC1$MX$Tmp2Als$mag$f | ✔ | mo_oltc_temp_oil_long_term_diff__high_high__limit | 10232
OLTC Long Term Difference in Oil Temperature main tank-OLTC (°C) High Alarm Limit | Models | 0 – 20 |  | 10233 | FLOAT32 | 1 |  | 30 | 12217 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | Tmp2Wrs |  | mag | f | MO/SLTC1$MX$Tmp2Wrs$mag$f | ✔ | mo_oltc_temp_oil_long_term_diff__high__limit | 10234
OLTC Operations per Hours High-High Alarm Limit | Models | 5 – 100 |  | 10235 | FLOAT32 | 1 |  | 30 | 12218 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | OpRte1Als |  | mag | f | MO/SLTC1$MX$OpRte1Als$mag$f | ✔ | mo_oltc_tp_operations_per_hour__high_high__limit | 10236
OLTC Operations per Hours High Alarm Limit | Models | 5 – 100 |  | 10237 | FLOAT32 | 1 |  | 30 | 12219 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | OpRte1Wrs |  | mag | f | MO/SLTC1$MX$OpRte1Wrs$mag$f | ✔ | mo_oltc_tp_operations_per_hour__high__limit | 10238
OLTC Operations per Day High-High Alarm Limit | Models | 20 – 1000 |  | 10239 | FLOAT32 | 1 |  | 30 | 12220 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | OpRte2Als |  | mag | f | MO/SLTC1$MX$OpRte2Als$mag$f | ✔ | mo_oltc_tp_operations_per_day__high_high__limit | 10240
OLTC Operations per Day High Alarm Limit | Models | 20 – 1000 |  | 10241 | FLOAT32 | 1 |  | 30 | 12221 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | OpRte2Wrs |  | mag | f | MO/SLTC1$MX$OpRte2Wrs$mag$f | ✔ | mo_oltc_tp_operations_per_day__high__limit | 10242
OLTC Motor Torque Total Time (%) High-High Alarm Limit | Models | 1 – 50 |  | 10243 | FLOAT32 | 1 |  | 30 | 12222 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | TorqTm1Als |  | mag | f | MO/SLTC1$MX$TorqTm1Als$mag$f | ✔ | mo_oltc_torque_total_time_pct__high_high__limit | 10244
OLTC Motor Torque Total Time (%) High Alarm Limit | Models | 1 – 50 |  | 10245 | FLOAT32 | 1 |  | 30 | 12223 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | TorqTm1Wrs |  | mag | f | MO/SLTC1$MX$TorqTm1Wrs$mag$f | ✔ | mo_oltc_torque_total_time_pct__high__limit | 10246
OLTC Motor Torque In-Rush Time (%) High-High Alarm Limit | Models | 1 – 50 |  | 10247 | FLOAT32 | 1 |  | 30 | 12224 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | TorqTm2Als |  | mag | f | MO/SLTC1$MX$TorqTm2Als$mag$f | ✔ | mo_oltc_torque_inrush_time_pct__high_high__limit | 10248
OLTC Motor Torque In-Rush Time (%) High Alarm Limit | Models | 1 – 50 |  | 10249 | FLOAT32 | 1 |  | 30 | 12225 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | TorqTm2Wrs |  | mag | f | MO/SLTC1$MX$TorqTm2Wrs$mag$f | ✔ | mo_oltc_torque_inrush_time_pct__high__limit | 10250
OLTC Motor Torque Maximum 1 (%) High-High Alarm Limit | Models | 1 – 50 |  | 10251 | FLOAT32 | 1 |  | 30 | 12226 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | Torq1Als |  | mag | f | MO/SLTC1$MX$Torq1Als$mag$f | ✔ | mo_oltc_torque_max_pwr1_pct__high_high__limit | 10252
OLTC Motor Torque Maximum 1 (%) High Alarm Limit | Models | 1 – 50 |  | 10253 | FLOAT32 | 1 |  | 30 | 12227 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | Torq1Wrs |  | mag | f | MO/SLTC1$MX$Torq1Wrs$mag$f | ✔ | mo_oltc_torque_max_pwr1_pct__high__limit | 10254
OLTC Motor Torque Maximum 2 (%) High-High Alarm Limit | Models | 1 – 50 |  | 10255 | FLOAT32 | 1 |  | 30 | 12228 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | Torq2Als |  | mag | f | MO/SLTC1$MX$Torq2Als$mag$f | ✔ | mo_oltc_torque_max_pwr2_pct__high_high__limit | 10256
OLTC Motor Torque Maximum 2 (%) High Alarm Limit | Models | 1 – 50 |  | 10257 | FLOAT32 | 1 |  | 30 | 12229 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | Torq2Wrs |  | mag | f | MO/SLTC1$MX$Torq2Wrs$mag$f | ✔ | mo_oltc_torque_max_pwr2_pct__high__limit | 10258
OLTC Motor Torque Maximum 3 (%) High-High Alarm Limit | Models | 1 – 50 |  | 10259 | FLOAT32 | 1 |  | 30 | 12230 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | Torq3Als |  | mag | f | MO/SLTC1$MX$Torq3Als$mag$f | ✔ | mo_oltc_torque_max_pwr3_pct__high_high__limit | 10260
OLTC Motor Torque Maximum 3 (%) High Alarm Limit | Models | 1 – 50 |  | 10261 | FLOAT32 | 1 |  | 30 | 12231 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | Torq3Wrs |  | mag | f | MO/SLTC1$MX$Torq3Wrs$mag$f | ✔ | mo_oltc_torque_max_pwr3_pct__high__limit | 10262
OLTC Motor Average Torque (%) High-High Alarm Limit | Models | 1 – 50 |  | 10263 | FLOAT32 | 1 |  | 30 | 12232 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | TorqAvgAls |  | mag | f | MO/SLTC1$MX$TorqAvgAls$mag$f | ✔ | mo_oltc_torque_avg_pwr_pct__high_high__limit | 10264
OLTC Motor Average Torque (%) High Alarm Limit | Models | 1 – 50 |  | 10265 | FLOAT32 | 1 |  | 30 | 12233 | 3 | 5 | 7 | ✔ | Disabled |  | MO | SLTC1 | MX | TorqAvgWrs |  | mag | f | MO/SLTC1$MX$TorqAvgWrs$mag$f | ✔ | mo_oltc_torque_avg_pwr_pct__high__limit | 10266
TH Cumulative Aging (hour) | Models | 0 - 4,294,967,295 |  | 10399 | UINT32 | 1 |  | 30 | 12400 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn1 |  | stVal |  | MO/GGIO4$ST$IntIn1$stVal | ✔ | mo_iam_cumulative_aging | 10400
Cooling Bank 1 User Operating Time (sec) | Models | 0 - 4,294,967,295 |  | 10401 | UINT32 | 1 |  | 30 | 12401 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn2 |  | stVal |  | MO/GGIO4$ST$IntIn2$stVal | ✔ | mo_csm_cooling_bank_1_user_operating_time | 10402
Cooling Bank 2 User Operating Time (sec) | Models | 0 - 4,294,967,295 |  | 10403 | UINT32 | 1 |  | 30 | 12402 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn3 |  | stVal |  | MO/GGIO4$ST$IntIn3$stVal | ✔ | mo_csm_cooling_bank_2_user_operating_time | 10404
Cooling Bank 3 User Operating Time (sec) | Models | 0 - 4,294,967,295 |  | 10405 | UINT32 | 1 |  | 30 | 12403 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn4 |  | stVal |  | MO/GGIO4$ST$IntIn4$stVal | ✔ | mo_csm_cooling_bank_3_user_operating_time | 10406
Cooling Bank 4 User Operating Time (sec) | Models | 0 - 4,294,967,295 |  | 10407 | UINT32 | 1 |  | 30 | 12404 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn5 |  | stVal |  | MO/GGIO4$ST$IntIn5$stVal | ✔ | mo_csm_cooling_bank_4_user_operating_time | 10408
Cooling Bank 1 Service Operating Time (sec) | Models | 0 - 4,294,967,295 |  | 10409 | UINT32 | 1 |  | 30 | 12405 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn6 |  | stVal |  | MO/GGIO4$ST$IntIn6$stVal | ✔ | mo_csm_cooling_bank_1_service_operating_time | 10410
Cooling Bank 2 Service Operating Time (sec) | Models | 0 - 4,294,967,295 |  | 10411 | UINT32 | 1 |  | 30 | 12406 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn7 |  | stVal |  | MO/GGIO4$ST$IntIn7$stVal | ✔ | mo_csm_cooling_bank_2_service_operating_time | 10412
Cooling Bank 3 Service Operating Time (sec) | Models | 0 - 4,294,967,295 |  | 10413 | UINT32 | 1 |  | 30 | 12407 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn8 |  | stVal |  | MO/GGIO4$ST$IntIn8$stVal | ✔ | mo_csm_cooling_bank_3_service_operating_time | 10414
Cooling Bank 4 Service Operating Time (sec) | Models | 0 - 4,294,967,295 |  | 10415 | UINT32 | 1 |  | 30 | 12408 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn9 |  | stVal |  | MO/GGIO4$ST$IntIn9$stVal | ✔ | mo_csm_cooling_bank_4_service_operating_time | 10416
Cooling Bank 1 Continuous Nonoperational time (sec) | Models | 0 - 4,294,967,295 |  | 10417 | UINT32 | 1 |  | 30 | 12409 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn10 |  | stVal |  | MO/GGIO4$ST$IntIn10$stVal | ✔ | mo_csm_cooling_bank_1_continuous_nonoperational_time | 10418
Cooling Bank 2 Continuous Nonoperational time (sec) | Models | 0 - 4,294,967,295 |  | 10419 | UINT32 | 1 |  | 30 | 12410 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn11 |  | stVal |  | MO/GGIO4$ST$IntIn11$stVal | ✔ | mo_csm_cooling_bank_2_continuous_nonoperational_time | 10420
Cooling Bank 3 Continuous Nonoperational time (sec) | Models | 0 - 4,294,967,295 |  | 10421 | UINT32 | 1 |  | 30 | 12411 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn12 |  | stVal |  | MO/GGIO4$ST$IntIn12$stVal | ✔ | mo_csm_cooling_bank_3_continuous_nonoperational_time | 10422
Cooling Bank 4 Continuous Nonoperational time (sec) | Models | 0 - 4,294,967,295 |  | 10423 | UINT32 | 1 |  | 30 | 12412 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn13 |  | stVal |  | MO/GGIO4$ST$IntIn13$stVal | ✔ | mo_csm_cooling_bank_4_continuous_nonoperational_time | 10424
COOL Cooling Bank 1 Continuous Nonoperational time (Hours) | Models | 0 - 4,294,967,295 |  | 10425 | UINT32 | 1 |  | 30 | 12413 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn14 |  | stVal |  | MO/GGIO4$ST$IntIn14$stVal | ✔ | mo_csm_cooling_bank_1_continuous_nonoperational_time_hour | 10426
COOL Cooling Bank 2 Continuous Nonoperational time (Hours) | Models | 0 - 4,294,967,295 |  | 10427 | UINT32 | 1 |  | 30 | 12414 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn15 |  | stVal |  | MO/GGIO4$ST$IntIn15$stVal | ✔ | mo_csm_cooling_bank_2_continuous_nonoperational_time_hour | 10428
COOL Cooling Bank 3 Continuous Nonoperational time (Hours) | Models | 0 - 4,294,967,295 |  | 10429 | UINT32 | 1 |  | 30 | 12415 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn16 |  | stVal |  | MO/GGIO4$ST$IntIn16$stVal | ✔ | mo_csm_cooling_bank_3_continuous_nonoperational_time_hour | 10430
COOL Cooling Bank 4 Continuous Nonoperational time (Hours) | Models | 0 - 4,294,967,295 |  | 10431 | UINT32 | 1 |  | 30 | 12416 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn17 |  | stVal |  | MO/GGIO4$ST$IntIn17$stVal | ✔ | mo_csm_cooling_bank_4_continuous_nonoperational_time_hour | 10432
Cooling Bank 1 User Number of Switching | Models | 0 - 4,294,967,295 |  | 10433 | UINT32 | 1 |  | 30 | 12417 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn18 |  | stVal |  | MO/GGIO4$ST$IntIn18$stVal | ✔ | mo_csm_cooling_bank_1_user_number_switching | 10434
Cooling Bank 2 User Number of Switching | Models | 0 - 4,294,967,295 |  | 10435 | UINT32 | 1 |  | 30 | 12418 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn19 |  | stVal |  | MO/GGIO4$ST$IntIn19$stVal | ✔ | mo_csm_cooling_bank_2_user_number_switching | 10436
Cooling Bank 3 User Number of Switching | Models | 0 - 4,294,967,295 |  | 10437 | UINT32 | 1 |  | 30 | 12419 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn20 |  | stVal |  | MO/GGIO4$ST$IntIn20$stVal | ✔ | mo_csm_cooling_bank_3_user_number_switching | 10438
Cooling Bank 4 User Number of Switching | Models | 0 - 4,294,967,295 |  | 10439 | UINT32 | 1 |  | 30 | 12420 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn21 |  | stVal |  | MO/GGIO4$ST$IntIn21$stVal | ✔ | mo_csm_cooling_bank_4_user_number_switching | 10440
Cooling Bank 1 Service Number of Switching | Models | 0 - 4,294,967,295 |  | 10441 | UINT32 | 1 |  | 30 | 12421 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn22 |  | stVal |  | MO/GGIO4$ST$IntIn22$stVal | ✔ | mo_csm_cooling_bank_1_service_number_switching | 10442
Cooling Bank 2 Service Number of Switching | Models | 0 - 4,294,967,295 |  | 10443 | UINT32 | 1 |  | 30 | 12422 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn23 |  | stVal |  | MO/GGIO4$ST$IntIn23$stVal | ✔ | mo_csm_cooling_bank_2_service_number_switching | 10444
Cooling Bank 3 Service Number of Switching | Models | 0 - 4,294,967,295 |  | 10445 | UINT32 | 1 |  | 30 | 12423 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn24 |  | stVal |  | MO/GGIO4$ST$IntIn24$stVal | ✔ | mo_csm_cooling_bank_3_service_number_switching | 10446
Cooling Bank 4 Service Number of Switching | Models | 0 - 4,294,967,295 |  | 10447 | UINT32 | 1 |  | 30 | 12424 | 2 | 1 | 3 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn25 |  | stVal |  | MO/GGIO4$ST$IntIn25$stVal | ✔ | mo_csm_cooling_bank_4_service_number_switching | 10448
OLTC Total number of OLTC operations | Models | 0 - 4,294,967,295 |  | 10449 | UINT32 | 1 |  | 30 | 12425 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | OpCnt1 |  | stVal |  | MO/YLTC1$ST$OpCnt1$stVal | ✔ | mo_oltc_tp_operations | 10450
OLTC Total number of OLTC reversing operations | Models | 0 - 4,294,967,295 |  | 10451 | UINT32 | 1 |  | 30 | 12426 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | OpCnt2 |  | stVal |  | MO/YLTC1$ST$OpCnt2$stVal | ✔ | mo_oltc_tp_reversing_operations | 10452
OLTC Total operating time | Models | 0 - 4,294,967,295 |  | 10453 | UINT32 | 1 |  | 30 | 12427 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | OpTm |  | stVal |  | MO/YLTC1$ST$OpTm$stVal | ✔ | mo_oltc_tp_total_operating_time | 10454
OLTC Tap Position Counter 1 | Models | 0 - 4,294,967,295 |  | 10455 | UINT32 | 1 |  | 30 | 12428 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr1 |  | stVal |  | MO/YLTC1$ST$PosCtr1$stVal | ✔ | mo_oltc_tp_tap_position_counter_1 | 10456
OLTC Tap Position Counter 2 | Models | 0 - 4,294,967,295 |  | 10457 | UINT32 | 1 |  | 30 | 12429 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr2 |  | stVal |  | MO/YLTC1$ST$PosCtr2$stVal | ✔ | mo_oltc_tp_tap_position_counter_2 | 10458
OLTC Tap Position Counter 3 | Models | 0 - 4,294,967,295 |  | 10459 | UINT32 | 1 |  | 30 | 12430 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr3 |  | stVal |  | MO/YLTC1$ST$PosCtr3$stVal | ✔ | mo_oltc_tp_tap_position_counter_3 | 10460
OLTC Tap Position Counter 4 | Models | 0 - 4,294,967,295 |  | 10461 | UINT32 | 1 |  | 30 | 12431 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr4 |  | stVal |  | MO/YLTC1$ST$PosCtr4$stVal | ✔ | mo_oltc_tp_tap_position_counter_4 | 10462
OLTC Tap Position Counter 5 | Models | 0 - 4,294,967,295 |  | 10463 | UINT32 | 1 |  | 30 | 12432 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr5 |  | stVal |  | MO/YLTC1$ST$PosCtr5$stVal | ✔ | mo_oltc_tp_tap_position_counter_5 | 10464
OLTC Tap Position Counter 6 | Models | 0 - 4,294,967,295 |  | 10465 | UINT32 | 1 |  | 30 | 12433 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr6 |  | stVal |  | MO/YLTC1$ST$PosCtr6$stVal | ✔ | mo_oltc_tp_tap_position_counter_6 | 10466
OLTC Tap Position Counter 7 | Models | 0 - 4,294,967,295 |  | 10467 | UINT32 | 1 |  | 30 | 12434 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr7 |  | stVal |  | MO/YLTC1$ST$PosCtr7$stVal | ✔ | mo_oltc_tp_tap_position_counter_7 | 10468
OLTC Tap Position Counter 8 | Models | 0 - 4,294,967,295 |  | 10469 | UINT32 | 1 |  | 30 | 12435 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr8 |  | stVal |  | MO/YLTC1$ST$PosCtr8$stVal | ✔ | mo_oltc_tp_tap_position_counter_8 | 10470
OLTC Tap Position Counter 9 | Models | 0 - 4,294,967,295 |  | 10471 | UINT32 | 1 |  | 30 | 12436 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr9 |  | stVal |  | MO/YLTC1$ST$PosCtr9$stVal | ✔ | mo_oltc_tp_tap_position_counter_9 | 10472
OLTC Tap Position Counter 10 | Models | 0 - 4,294,967,295 |  | 10473 | UINT32 | 1 |  | 30 | 12437 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr10 |  | stVal |  | MO/YLTC1$ST$PosCtr10$stVal | ✔ | mo_oltc_tp_tap_position_counter_10 | 10474
OLTC Tap Position Counter 11 | Models | 0 - 4,294,967,295 |  | 10475 | UINT32 | 1 |  | 30 | 12438 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr11 |  | stVal |  | MO/YLTC1$ST$PosCtr11$stVal | ✔ | mo_oltc_tp_tap_position_counter_11 | 10476
OLTC Tap Position Counter 12 | Models | 0 - 4,294,967,295 |  | 10477 | UINT32 | 1 |  | 30 | 12439 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr12 |  | stVal |  | MO/YLTC1$ST$PosCtr12$stVal | ✔ | mo_oltc_tp_tap_position_counter_12 | 10478
OLTC Tap Position Counter 13 | Models | 0 - 4,294,967,295 |  | 10479 | UINT32 | 1 |  | 30 | 12440 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr13 |  | stVal |  | MO/YLTC1$ST$PosCtr13$stVal | ✔ | mo_oltc_tp_tap_position_counter_13 | 10480
OLTC Tap Position Counter 14 | Models | 0 - 4,294,967,295 |  | 10481 | UINT32 | 1 |  | 30 | 12441 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr14 |  | stVal |  | MO/YLTC1$ST$PosCtr14$stVal | ✔ | mo_oltc_tp_tap_position_counter_14 | 10482
OLTC Tap Position Counter 15 | Models | 0 - 4,294,967,295 |  | 10483 | UINT32 | 1 |  | 30 | 12442 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr15 |  | stVal |  | MO/YLTC1$ST$PosCtr15$stVal | ✔ | mo_oltc_tp_tap_position_counter_15 | 10484
OLTC Tap Position Counter 16 | Models | 0 - 4,294,967,295 |  | 10485 | UINT32 | 1 |  | 30 | 12443 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr16 |  | stVal |  | MO/YLTC1$ST$PosCtr16$stVal | ✔ | mo_oltc_tp_tap_position_counter_16 | 10486
OLTC Tap Position Counter 17 | Models | 0 - 4,294,967,295 |  | 10487 | UINT32 | 1 |  | 30 | 12444 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr17 |  | stVal |  | MO/YLTC1$ST$PosCtr17$stVal | ✔ | mo_oltc_tp_tap_position_counter_17 | 10488
OLTC Tap Position Counter 18 | Models | 0 - 4,294,967,295 |  | 10489 | UINT32 | 1 |  | 30 | 12445 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr18 |  | stVal |  | MO/YLTC1$ST$PosCtr18$stVal | ✔ | mo_oltc_tp_tap_position_counter_18 | 10490
OLTC Tap Position Counter 19 | Models | 0 - 4,294,967,295 |  | 10491 | UINT32 | 1 |  | 30 | 12446 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr19 |  | stVal |  | MO/YLTC1$ST$PosCtr19$stVal | ✔ | mo_oltc_tp_tap_position_counter_19 | 10492
OLTC Tap Position Counter 20 | Models | 0 - 4,294,967,295 |  | 10493 | UINT32 | 1 |  | 30 | 12447 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr20 |  | stVal |  | MO/YLTC1$ST$PosCtr20$stVal | ✔ | mo_oltc_tp_tap_position_counter_20 | 10494
OLTC Tap Position Counter 21 | Models | 0 - 4,294,967,295 |  | 10495 | UINT32 | 1 |  | 30 | 12448 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr21 |  | stVal |  | MO/YLTC1$ST$PosCtr21$stVal | ✔ | mo_oltc_tp_tap_position_counter_21 | 10496
OLTC Tap Position Counter 22 | Models | 0 - 4,294,967,295 |  | 10497 | UINT32 | 1 |  | 30 | 12449 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr22 |  | stVal |  | MO/YLTC1$ST$PosCtr22$stVal | ✔ | mo_oltc_tp_tap_position_counter_22 | 10498
OLTC Tap Position Counter 23 | Models | 0 - 4,294,967,295 |  | 10499 | UINT32 | 1 |  | 30 | 12450 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr23 |  | stVal |  | MO/YLTC1$ST$PosCtr23$stVal | ✔ | mo_oltc_tp_tap_position_counter_23 | 10500
OLTC Tap Position Counter 24 | Models | 0 - 4,294,967,295 |  | 10501 | UINT32 | 1 |  | 30 | 12451 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr24 |  | stVal |  | MO/YLTC1$ST$PosCtr24$stVal | ✔ | mo_oltc_tp_tap_position_counter_24 | 10502
OLTC Tap Position Counter 25 | Models | 0 - 4,294,967,295 |  | 10503 | UINT32 | 1 |  | 30 | 12452 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr25 |  | stVal |  | MO/YLTC1$ST$PosCtr25$stVal | ✔ | mo_oltc_tp_tap_position_counter_25 | 10504
OLTC Tap Position Counter 26 | Models | 0 - 4,294,967,295 |  | 10505 | UINT32 | 1 |  | 30 | 12453 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr26 |  | stVal |  | MO/YLTC1$ST$PosCtr26$stVal | ✔ | mo_oltc_tp_tap_position_counter_26 | 10506
OLTC Tap Position Counter 27 | Models | 0 - 4,294,967,295 |  | 10507 | UINT32 | 1 |  | 30 | 12454 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr27 |  | stVal |  | MO/YLTC1$ST$PosCtr27$stVal | ✔ | mo_oltc_tp_tap_position_counter_27 | 10508
OLTC Tap Position Counter 28 | Models | 0 - 4,294,967,295 |  | 10509 | UINT32 | 1 |  | 30 | 12455 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr28 |  | stVal |  | MO/YLTC1$ST$PosCtr28$stVal | ✔ | mo_oltc_tp_tap_position_counter_28 | 10510
OLTC Tap Position Counter 29 | Models | 0 - 4,294,967,295 |  | 10511 | UINT32 | 1 |  | 30 | 12456 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr29 |  | stVal |  | MO/YLTC1$ST$PosCtr29$stVal | ✔ | mo_oltc_tp_tap_position_counter_29 | 10512
OLTC Tap Position Counter 30 | Models | 0 - 4,294,967,295 |  | 10513 | UINT32 | 1 |  | 30 | 12457 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr30 |  | stVal |  | MO/YLTC1$ST$PosCtr30$stVal | ✔ | mo_oltc_tp_tap_position_counter_30 | 10514
OLTC Tap Position Counter 31 | Models | 0 - 4,294,967,295 |  | 10515 | UINT32 | 1 |  | 30 | 12458 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr31 |  | stVal |  | MO/YLTC1$ST$PosCtr31$stVal | ✔ | mo_oltc_tp_tap_position_counter_31 | 10516
OLTC Tap Position Counter 32 | Models | 0 - 4,294,967,295 |  | 10517 | UINT32 | 1 |  | 30 | 12459 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr32 |  | stVal |  | MO/YLTC1$ST$PosCtr32$stVal | ✔ | mo_oltc_tp_tap_position_counter_32 | 10518
OLTC Tap Position Counter 33 | Models | 0 - 4,294,967,295 |  | 10519 | UINT32 | 1 |  | 30 | 12460 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr33 |  | stVal |  | MO/YLTC1$ST$PosCtr33$stVal | ✔ | mo_oltc_tp_tap_position_counter_33 | 10520
OLTC Tap Position Counter 34 | Models | 0 - 4,294,967,295 |  | 10521 | UINT32 | 1 |  | 30 | 12461 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr34 |  | stVal |  | MO/YLTC1$ST$PosCtr34$stVal | ✔ | mo_oltc_tp_tap_position_counter_34 | 10522
OLTC Tap Position Counter 35 | Models | 0 - 4,294,967,295 |  | 10523 | UINT32 | 1 |  | 30 | 12462 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosCtr35 |  | stVal |  | MO/YLTC1$ST$PosCtr35$stVal | ✔ | mo_oltc_tp_tap_position_counter_35 | 10524
OLTC Tap Position 1 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10525 | UINT32 | 1 |  | 30 | 12463 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm1 |  | stVal |  | MO/YLTC1$ST$PosTm1$stVal | ✔ | mo_oltc_tp_tap_position_time_1 | 10526
OLTC Tap Position 2 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10527 | UINT32 | 1 |  | 30 | 12464 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm2 |  | stVal |  | MO/YLTC1$ST$PosTm2$stVal | ✔ | mo_oltc_tp_tap_position_time_2 | 10528
OLTC Tap Position 3 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10529 | UINT32 | 1 |  | 30 | 12465 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm3 |  | stVal |  | MO/YLTC1$ST$PosTm3$stVal | ✔ | mo_oltc_tp_tap_position_time_3 | 10530
OLTC Tap Position 4 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10531 | UINT32 | 1 |  | 30 | 12466 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm4 |  | stVal |  | MO/YLTC1$ST$PosTm4$stVal | ✔ | mo_oltc_tp_tap_position_time_4 | 10532
OLTC Tap Position 5 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10533 | UINT32 | 1 |  | 30 | 12467 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm5 |  | stVal |  | MO/YLTC1$ST$PosTm5$stVal | ✔ | mo_oltc_tp_tap_position_time_5 | 10534
OLTC Tap Position 6 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10535 | UINT32 | 1 |  | 30 | 12468 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm6 |  | stVal |  | MO/YLTC1$ST$PosTm6$stVal | ✔ | mo_oltc_tp_tap_position_time_6 | 10536
OLTC Tap Position 7 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10537 | UINT32 | 1 |  | 30 | 12469 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm7 |  | stVal |  | MO/YLTC1$ST$PosTm7$stVal | ✔ | mo_oltc_tp_tap_position_time_7 | 10538
OLTC Tap Position 8 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10539 | UINT32 | 1 |  | 30 | 12470 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm8 |  | stVal |  | MO/YLTC1$ST$PosTm8$stVal | ✔ | mo_oltc_tp_tap_position_time_8 | 10540
OLTC Tap Position 9 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10541 | UINT32 | 1 |  | 30 | 12471 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm9 |  | stVal |  | MO/YLTC1$ST$PosTm9$stVal | ✔ | mo_oltc_tp_tap_position_time_9 | 10542
OLTC Tap Position 10 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10543 | UINT32 | 1 |  | 30 | 12472 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm10 |  | stVal |  | MO/YLTC1$ST$PosTm10$stVal | ✔ | mo_oltc_tp_tap_position_time_10 | 10544
OLTC Tap Position 11 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10545 | UINT32 | 1 |  | 30 | 12473 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm11 |  | stVal |  | MO/YLTC1$ST$PosTm11$stVal | ✔ | mo_oltc_tp_tap_position_time_11 | 10546
OLTC Tap Position 12 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10547 | UINT32 | 1 |  | 30 | 12474 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm12 |  | stVal |  | MO/YLTC1$ST$PosTm12$stVal | ✔ | mo_oltc_tp_tap_position_time_12 | 10548
OLTC Tap Position 13 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10549 | UINT32 | 1 |  | 30 | 12475 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm13 |  | stVal |  | MO/YLTC1$ST$PosTm13$stVal | ✔ | mo_oltc_tp_tap_position_time_13 | 10550
OLTC Tap Position 14 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10551 | UINT32 | 1 |  | 30 | 12476 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm14 |  | stVal |  | MO/YLTC1$ST$PosTm14$stVal | ✔ | mo_oltc_tp_tap_position_time_14 | 10552
OLTC Tap Position 15 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10553 | UINT32 | 1 |  | 30 | 12477 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm15 |  | stVal |  | MO/YLTC1$ST$PosTm15$stVal | ✔ | mo_oltc_tp_tap_position_time_15 | 10554
OLTC Tap Position 16 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10555 | UINT32 | 1 |  | 30 | 12478 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm16 |  | stVal |  | MO/YLTC1$ST$PosTm16$stVal | ✔ | mo_oltc_tp_tap_position_time_16 | 10556
OLTC Tap Position 17 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10557 | UINT32 | 1 |  | 30 | 12479 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm17 |  | stVal |  | MO/YLTC1$ST$PosTm17$stVal | ✔ | mo_oltc_tp_tap_position_time_17 | 10558
OLTC Tap Position 18 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10559 | UINT32 | 1 |  | 30 | 12480 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm18 |  | stVal |  | MO/YLTC1$ST$PosTm18$stVal | ✔ | mo_oltc_tp_tap_position_time_18 | 10560
OLTC Tap Position 19 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10561 | UINT32 | 1 |  | 30 | 12481 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm19 |  | stVal |  | MO/YLTC1$ST$PosTm19$stVal | ✔ | mo_oltc_tp_tap_position_time_19 | 10562
OLTC Tap Position 20 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10563 | UINT32 | 1 |  | 30 | 12482 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm20 |  | stVal |  | MO/YLTC1$ST$PosTm20$stVal | ✔ | mo_oltc_tp_tap_position_time_20 | 10564
OLTC Tap Position 21 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10565 | UINT32 | 1 |  | 30 | 12483 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm21 |  | stVal |  | MO/YLTC1$ST$PosTm21$stVal | ✔ | mo_oltc_tp_tap_position_time_21 | 10566
OLTC Tap Position 22 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10567 | UINT32 | 1 |  | 30 | 12484 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm22 |  | stVal |  | MO/YLTC1$ST$PosTm22$stVal | ✔ | mo_oltc_tp_tap_position_time_22 | 10568
OLTC Tap Position 23 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10569 | UINT32 | 1 |  | 30 | 12485 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm23 |  | stVal |  | MO/YLTC1$ST$PosTm23$stVal | ✔ | mo_oltc_tp_tap_position_time_23 | 10570
OLTC Tap Position 24 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10571 | UINT32 | 1 |  | 30 | 12486 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm24 |  | stVal |  | MO/YLTC1$ST$PosTm24$stVal | ✔ | mo_oltc_tp_tap_position_time_24 | 10572
OLTC Tap Position 25 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10573 | UINT32 | 1 |  | 30 | 12487 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm25 |  | stVal |  | MO/YLTC1$ST$PosTm25$stVal | ✔ | mo_oltc_tp_tap_position_time_25 | 10574
OLTC Tap Position 26 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10575 | UINT32 | 1 |  | 30 | 12488 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm26 |  | stVal |  | MO/YLTC1$ST$PosTm26$stVal | ✔ | mo_oltc_tp_tap_position_time_26 | 10576
OLTC Tap Position 27 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10577 | UINT32 | 1 |  | 30 | 12489 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm27 |  | stVal |  | MO/YLTC1$ST$PosTm27$stVal | ✔ | mo_oltc_tp_tap_position_time_27 | 10578
OLTC Tap Position 28 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10579 | UINT32 | 1 |  | 30 | 12490 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm28 |  | stVal |  | MO/YLTC1$ST$PosTm28$stVal | ✔ | mo_oltc_tp_tap_position_time_28 | 10580
OLTC Tap Position 29 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10581 | UINT32 | 1 |  | 30 | 12491 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm29 |  | stVal |  | MO/YLTC1$ST$PosTm29$stVal | ✔ | mo_oltc_tp_tap_position_time_29 | 10582
OLTC Tap Position 30 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10583 | UINT32 | 1 |  | 30 | 12492 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm30 |  | stVal |  | MO/YLTC1$ST$PosTm30$stVal | ✔ | mo_oltc_tp_tap_position_time_30 | 10584
OLTC Tap Position 31 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10585 | UINT32 | 1 |  | 30 | 12493 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm31 |  | stVal |  | MO/YLTC1$ST$PosTm31$stVal | ✔ | mo_oltc_tp_tap_position_time_31 | 10586
OLTC Tap Position 32 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10587 | UINT32 | 1 |  | 30 | 12494 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm32 |  | stVal |  | MO/YLTC1$ST$PosTm32$stVal | ✔ | mo_oltc_tp_tap_position_time_32 | 10588
OLTC Tap Position 33 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10589 | UINT32 | 1 |  | 30 | 12495 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm33 |  | stVal |  | MO/YLTC1$ST$PosTm33$stVal | ✔ | mo_oltc_tp_tap_position_time_33 | 10590
OLTC Tap Position 34 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10591 | UINT32 | 1 |  | 30 | 12496 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm34 |  | stVal |  | MO/YLTC1$ST$PosTm34$stVal | ✔ | mo_oltc_tp_tap_position_time_34 | 10592
OLTC Tap Position 35 Cumulative Time since Last Recording (sec) | Models | 0 - 4,294,967,295 |  | 10593 | UINT32 | 1 |  | 30 | 12497 | 2 | 1 | 3 | ✔ | Disabled |  | MO | YLTC1 | ST | PosTm35 |  | stVal |  | MO/YLTC1$ST$PosTm35$stVal | ✔ | mo_oltc_tp_tap_position_time_35 | 10594
TH Remaining time until Moisture Content in Pressboard Barrier model reliable (day) | Models | 0 - 65,535 |  | 10699 | UINT16 | 1 |  | 30 | 12700 | 2 | 2 | 4 | ✔ | Disabled |  | MO | SPTR1 | ST | InsTmms2 |  | stVal |  | MO/SPTR1$ST$InsTmms2$stVal | ✔ | mo_mstinsbar_remaining_time_until_reliable | 10700
TH Transformer Cumulative Service Time (day) | Models | 0 - 65,535 |  | 10700 | UINT16 | 1 |  | 30 | 12701 | 2 | 2 | 4 | ✔ | Disabled |  | MO | SPTR1 | ST | ServTm |  | stVal |  | MO/SPTR1$ST$ServTm$stVal | ✔ | mo_iam_cumulative_service_time | 10701
TH Overload time for Load factor (p.u.) = 1.1 (Min) | Models | 0 - 65,535 |  | 10701 | UINT16 | 1 |  | 30 | 12702 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlTm1 |  | stVal |  | MO/YPTR1$ST$OvlTm1$stVal | ✔ | mo_dlg_overload_time_11 | 10702
Overload factor for K (p.u.) = 1.1 (see Dynamic Loading Model Overload Factors below) | Models | 0 - 65,535 |  | 10702 | UINT16 | 1 |  | 30 | 12703 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlFact1 |  | stVal |  | MO/YPTR1$ST$OvlFact1$stVal | ✔ | mo_dlg_overload_factor_11 | 10703
TH Overload time for Load factor (p.u.) = 1.2 (Min) | Models | 0 - 65,535 |  | 10703 | UINT16 | 1 |  | 30 | 12704 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlTm2 |  | stVal |  | MO/YPTR1$ST$OvlTm2$stVal | ✔ | mo_dlg_overload_time_12 | 10704
Overload factor for K (p.u.) = 1.2 (see Dynamic Loading Model Overload Factors below) | Models | 0 - 65,535 |  | 10704 | UINT16 | 1 |  | 30 | 12705 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlFact2 |  | stVal |  | MO/YPTR1$ST$OvlFact2$stVal | ✔ | mo_dlg_overload_factor_12 | 10705
TH Overload time for Load factor (p.u.) = 1.3 (Min) | Models | 0 - 65,535 |  | 10705 | UINT16 | 1 |  | 30 | 12706 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlTm3 |  | stVal |  | MO/YPTR1$ST$OvlTm3$stVal | ✔ | mo_dlg_overload_time_13 | 10706
Overload factor for K (p.u.) = 1.3 (see Dynamic Loading Model Overload Factors below) | Models | 0 - 65,535 |  | 10706 | UINT16 | 1 |  | 30 | 12707 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlFact3 |  | stVal |  | MO/YPTR1$ST$OvlFact3$stVal | ✔ | mo_dlg_overload_factor_13 | 10707
TH Overload time for Load factor (p.u.) = 1.4 (Min) | Models | 0 - 65,535 |  | 10707 | UINT16 | 1 |  | 30 | 12708 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlTm4 |  | stVal |  | MO/YPTR1$ST$OvlTm4$stVal | ✔ | mo_dlg_overload_time_14 | 10708
Overload factor for K (p.u.) = 1.4 (see Dynamic Loading Model Overload Factors below) | Models | 0 - 65,535 |  | 10708 | UINT16 | 1 |  | 30 | 12709 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlFact4 |  | stVal |  | MO/YPTR1$ST$OvlFact4$stVal | ✔ | mo_dlg_overload_factor_14 | 10709
TH Overload time for Load factor (p.u.) = 1.5 (Min) | Models | 0 - 65,535 |  | 10709 | UINT16 | 1 |  | 30 | 12710 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlTm5 |  | stVal |  | MO/YPTR1$ST$OvlTm5$stVal | ✔ | mo_dlg_overload_time_15 | 10710
Overload factor for K (p.u.) = 1.5 (see Dynamic Loading Model Overload Factors below) | Models | 0 - 65,535 |  | 10710 | UINT16 | 1 |  | 30 | 12711 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlFact5 |  | stVal |  | MO/YPTR1$ST$OvlFact5$stVal | ✔ | mo_dlg_overload_factor_15 | 10711
TH Overload time for Load factor (p.u.) = 1.6 (Min) | Models | 0 - 65,535 |  | 10711 | UINT16 | 1 |  | 30 | 12712 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlTm6 |  | stVal |  | MO/YPTR1$ST$OvlTm6$stVal | ✔ | mo_dlg_overload_time_16 | 10712
Overload factor for K (p.u.) = 1.6 (see Dynamic Loading Model Overload Factors below) | Models | 0 - 65,535 |  | 10712 | UINT16 | 1 |  | 30 | 12713 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlFact6 |  | stVal |  | MO/YPTR1$ST$OvlFact6$stVal | ✔ | mo_dlg_overload_factor_16 | 10713
TH Overload time for Load factor (p.u.) = 1.7 (Min) | Models | 0 - 65,535 |  | 10713 | UINT16 | 1 |  | 30 | 12714 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlTm7 |  | stVal |  | MO/YPTR1$ST$OvlTm7$stVal | ✔ | mo_dlg_overload_time_17 | 10714
Overload factor for K (p.u.) = 1.7 (see Dynamic Loading Model Overload Factors below) | Models | 0 - 65,535 |  | 10714 | UINT16 | 1 |  | 30 | 12715 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlFact7 |  | stVal |  | MO/YPTR1$ST$OvlFact7$stVal | ✔ | mo_dlg_overload_factor_17 | 10715
TH Overload time for Load factor (p.u.) = 1.8 (Min) | Models | 0 - 65,535 |  | 10715 | UINT16 | 1 |  | 30 | 12716 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlTm8 |  | stVal |  | MO/YPTR1$ST$OvlTm8$stVal | ✔ | mo_dlg_overload_time_18 | 10716
Overload factor for K (p.u.) = 1.8 (see Dynamic Loading Model Overload Factors below) | Models | 0 - 65,535 |  | 10716 | UINT16 | 1 |  | 30 | 12717 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlFact8 |  | stVal |  | MO/YPTR1$ST$OvlFact8$stVal | ✔ | mo_dlg_overload_factor_18 | 10717
TH Overload time for Load factor (p.u.) = 1.9 (Min) | Models | 0 - 65,535 |  | 10717 | UINT16 | 1 |  | 30 | 12718 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlTm9 |  | stVal |  | MO/YPTR1$ST$OvlTm9$stVal | ✔ | mo_dlg_overload_time_19 | 10718
Overload factor for K (p.u.) = 1.9 (see Dynamic Loading Model Overload Factors below) | Models | 0 - 65,535 |  | 10718 | UINT16 | 1 |  | 30 | 12719 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlFact9 |  | stVal |  | MO/YPTR1$ST$OvlFact9$stVal | ✔ | mo_dlg_overload_factor_19 | 10719
TH Overload time for Load factor (p.u.) = 1.2 (Min) | Models | 0 - 65,535 |  | 10719 | UINT16 | 1 |  | 30 | 12720 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlTm10 |  | stVal |  | MO/YPTR1$ST$OvlTm10$stVal | ✔ | mo_dlg_overload_time_20 | 10720
Overload factor for K (p.u.) = 2.0 (see Dynamic Loading Model Overload Factors below) | Models | 0 - 65,535 |  | 10720 | UINT16 | 1 |  | 30 | 12721 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YPTR1 | ST | OvlFact10 |  | stVal |  | MO/YPTR1$ST$OvlFact10$stVal | ✔ | mo_dlg_overload_factor_20 | 10721
COOL Cooling Stage Currently in Service | Models | 0 - 65,535 |  | 10721 | UINT16 | 1 |  | 30 | 12722 | 2 | 2 | 4 | ✔ | Disabled |  | MO | GGIO4 | ST | IntIn26 |  | stVal |  | MO/GGIO4$ST$IntIn26$stVal | ✔ | mo_csm_cooling_stage | 10722
OLTC Current Tap (Mechanical) Position | Models | 0 - 65,535 |  | 10722 | UINT16 | 1 |  | 30 | 12723 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YLTC1 | ST | TapPos1 |  | stVal |  | MO/YLTC1$ST$TapPos1$stVal | ✔ | mo_oltc_tp_current_tap_position | 10723
OLTC Operations per Hour | Models | 0 - 65,535 |  | 10723 | UINT16 | 1 |  | 30 | 12724 | 2 | 2 | 4 | ✔ | Disabled |  | MO | SLTC1 | ST | OpRte1 |  | stVal |  | MO/SLTC1$ST$OpRte1$stVal | ✔ | mo_oltc_tp_operations_per_hour | 10724
OLTC Operations per Day | Models | 0 - 65,535 |  | 10724 | UINT16 | 1 |  | 30 | 12725 | 2 | 2 | 4 | ✔ | Disabled |  | MO | SLTC1 | ST | OpRte2 |  | stVal |  | MO/SLTC1$ST$OpRte2$stVal | ✔ | mo_oltc_tp_operations_per_day | 10725
OLTC Current Tap Electrical Position | Models | 0 - 65,535 |  | 10725 | UINT16 | 1 |  | 30 | 12726 | 2 | 2 | 4 | ✔ | Disabled |  | MO | YLTC1 | ST | TapPos2 |  | stVal |  | MO/YLTC1$ST$TapPos2$stVal | ✔ | mo_oltc_tp_current_tap_electrical_position | 10726
OLTC Final Electrical Tap Position | Models | 0 - 65,535 |  | 10726 | UINT16 | 1 |  | 30 | 12727 | 2 | 2 | 4 | ✔ | Active |  | MO | YLTC1 | ST | TapPos3 |  | stVal |  | MO/YLTC1$ST$TapPos3$stVal | ✔ | mo_oltc_final_elec_tap_pos | 10727
OLTC Previous Electrical Tap Position | Models | 0 - 65,535 |  | 10727 | UINT16 | 1 |  | 30 | 12728 | 2 | 2 | 4 | ✔ | Active |  | MO | YLTC1 | ST | TapPos4 |  | stVal |  | MO/YLTC1$ST$TapPos4$stVal | ✔ | mo_oltc_prev_elec_tap_pos | 10728
OLTC Electrical Tap Position Before Previous | Models | 0 - 65,535 |  | 10728 | UINT16 | 1 |  | 30 | 12729 | 2 | 2 | 4 | ✔ | Active |  | MO | YLTC1 | ST | TapPos5 |  | stVal |  | MO/YLTC1$ST$TapPos5$stVal | ✔ | mo_oltc_prev_prev_elec_tap_pos | 10729
Tap Position Group | Models | 0 - 65,535 |  | 10729 | UINT16 | 1 |  | 30 | 12730 | 2 | 2 | 4 | ✔ | Active |  | MO | YLTC1 | ST | TapPosGr |  | stVal |  | MO/YLTC1$ST$TapPosGr$stVal | ✔ | mo_oltc_tap_pos_group | 10730
BM Set1 Power Frequency (Hz) | BMT | 45-65 Hz |  | 10999 | FLOAT32 | 1 |  | 30 | 10000 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Frequency |  | mag | f | BMT/GGIO2$MX$Frequency$mag$f | ✔ | bm_1_frequency | 11000
BM Channel 1 Bushing Current | BMT | 0 - 4294967295 A |  | 11013 | FLOAT32 | 1 |  | 30 | 10007 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | LeakA1 |  | mag | f | BMT/ZBSH1$MX$LeakA1$mag$f | ✔ | bm_1_current_ch1 | 11014
BM Channel 2 Bushing Current | BMT | 0 - 4294967295 A |  | 11015 | FLOAT32 | 1 |  | 30 | 10008 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | LeakA2 |  | mag | f | BMT/ZBSH1$MX$LeakA2$mag$f | ✔ | bm_1_current_ch2 | 11016
BM Channel 3 Bushing Current | BMT | 0 - 4294967295 A |  | 11017 | FLOAT32 | 1 |  | 30 | 10009 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | LeakA3 |  | mag | f | BMT/ZBSH1$MX$LeakA3$mag$f | ✔ | bm_1_current_ch3 | 11018
BM Channel 4 Bushing Current | BMT | 0 - 4294967295 A |  | 11019 | FLOAT32 | 1 |  | 30 | 10010 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | LeakA4 |  | mag | f | BMT/ZBSH1$MX$LeakA4$mag$f | ✔ | bm_1_current_ch4 | 11020
BM Channel 5 Bushing Current | BMT | 0 - 4294967295 A |  | 11021 | FLOAT32 | 1 |  | 30 | 10011 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | LeakA5 |  | mag | f | BMT/ZBSH1$MX$LeakA5$mag$f | ✔ | bm_1_current_ch5 | 11022
BM Channel 6 Bushing Current | BMT | 0 - 4294967295 A |  | 11023 | FLOAT32 | 1 |  | 30 | 10012 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | LeakA6 |  | mag | f | BMT/ZBSH1$MX$LeakA6$mag$f | ✔ | bm_1_current_ch6 | 11024
BM Channel 1 Estimated ΔC1 | BMT | 0 - 4294967295 |  | 11025 | FLOAT32 | 1 |  | 30 | 10013 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React1 |  | mag | f | BMT/ZBSH1$MX$React1$mag$f | ✔ | bm_1_c1_ch1 | 11026
BM Channel 2 Estimated ΔC1 | BMT | 0 - 4294967295 |  | 11027 | FLOAT32 | 1 |  | 30 | 10014 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React2 |  | mag | f | BMT/ZBSH1$MX$React2$mag$f | ✔ | bm_1_c1_ch2 | 11028
BM Channel 3 Estimated ΔC1 | BMT | 0 - 4294967295 |  | 11029 | FLOAT32 | 1 |  | 30 | 10015 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React3 |  | mag | f | BMT/ZBSH1$MX$React3$mag$f | ✔ | bm_1_c1_ch3 | 11030
BM Channel 4 Estimated ΔC1 | BMT | 0 - 4294967295 |  | 11031 | FLOAT32 | 1 |  | 30 | 10016 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React4 |  | mag | f | BMT/ZBSH1$MX$React4$mag$f | ✔ | bm_1_c1_ch4 | 11032
BM Channel 5 Estimated ΔC1 | BMT | 0 - 4294967295 |  | 11033 | FLOAT32 | 1 |  | 30 | 10017 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React5 |  | mag | f | BMT/ZBSH1$MX$React5$mag$f | ✔ | bm_1_c1_ch5 | 11034
BM Channel 6 Estimated ΔC1 | BMT | 0 - 4294967295 |  | 11035 | FLOAT32 | 1 |  | 30 | 10018 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React6 |  | mag | f | BMT/ZBSH1$MX$React6$mag$f | ✔ | bm_1_c1_ch6 | 11036
BM Phase Angle Channels 1-2 | BMT | -180 - 180 |  | 11037 | FLOAT32 | 1 |  | 30 | 10019 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Phs12 |  | mag | f | BMT/GGIO2$MX$Phs12$mag$f | ✔ | bm_1_angle_ch12 | 11038
BM Phase Angle Channels 1-3 | BMT | -180 - 180 |  | 11039 | FLOAT32 | 1 |  | 30 | 10020 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Phs13 |  | mag | f | BMT/GGIO2$MX$Phs13$mag$f | ✔ | bm_1_angle_ch13 | 11040
BM Phase Angle Channels 4-5 | BMT | -180 - 180 |  | 11041 | FLOAT32 | 1 |  | 30 | 10021 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Phs45 |  | mag | f | BMT/GGIO2$MX$Phs45$mag$f | ✔ | bm_1_angle_ch45 | 11042
BM Phase Angle Channels 4-6 | BMT | -180 - 180 |  | 11043 | FLOAT32 | 1 |  | 30 | 10022 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Phs46 |  | mag | f | BMT/GGIO2$MX$Phs46$mag$f | ✔ | bm_1_angle_ch46 | 11044
PD Channel 1 PDI (mW) (Partial Discharge Intensity) | BMT | 0 - 4294967295 mW |  | 11071 | FLOAT32 | 1 |  | 30 | 10036 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdIdx1 |  | mag | f | BMT/SPDC1$MX$PdIdx1$mag$f | ✔ | bm_1_pdi_ch1 | 11072
PD Channel 2 PDI (mW) | BMT | 0 - 4294967295 mW |  | 11073 | FLOAT32 | 1 |  | 30 | 10037 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdIdx2 |  | mag | f | BMT/SPDC1$MX$PdIdx2$mag$f | ✔ | bm_1_pdi_ch2 | 11074
PD Channel 3 PDI (mW) | BMT | 0 - 4294967295 mW |  | 11075 | FLOAT32 | 1 |  | 30 | 10038 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdIdx3 |  | mag | f | BMT/SPDC1$MX$PdIdx3$mag$f | ✔ | bm_1_pdi_ch3 | 11076
PD Channel 1 Calculated PDI Without Discrimination (mW) | BMT | 0 - 4294967295 mW |  | 11077 | FLOAT32 | 1 |  | 30 | 10039 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdIdxN1 |  | mag | f | BMT/SPDC1$MX$PdIdxN1$mag$f | ✔ | bm_1_pdi_ch1_nless | 11078
PD Channel 2 Calculated PDI Without Discrimination (mW) | BMT | 0 - 4294967295 mW |  | 11079 | FLOAT32 | 1 |  | 30 | 10040 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdIdxN2 |  | mag | f | BMT/SPDC1$MX$PdIdxN2$mag$f | ✔ | bm_1_pdi_ch2_nless | 11080
PD Channel 3 Calculated PDI Without Discrimination (mW) | BMT | 0 - 4294967295 mW |  | 11081 | FLOAT32 | 1 |  | 30 | 10041 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdIdxN3 |  | mag | f | BMT/SPDC1$MX$PdIdxN3$mag$f | ✔ | bm_1_pdi_ch3_nless | 11082
PD Channel 1 Average Number of Events per Cycle | BMT | 0 - 4294967295 |  | 11083 | FLOAT32 | 1 |  | 30 | 10042 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdCnt1 |  | mag | f | BMT/SPDC1$MX$PdCnt1$mag$f | ✔ | bm_1_pd_count_ch1 | 11084
PD Channel 2 Average Number of Events per Cycle | BMT | 0 - 4294967295 |  | 11085 | FLOAT32 | 1 |  | 30 | 10043 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdCnt2 |  | mag | f | BMT/SPDC1$MX$PdCnt2$mag$f | ✔ | bm_1_pd_count_ch2 | 11086
PD Channel 3 Average Number of Events per Cycle | BMT | 0 - 4294967295 |  | 11087 | FLOAT32 | 1 |  | 30 | 10044 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdCnt3 |  | mag | f | BMT/SPDC1$MX$PdCnt3$mag$f | ✔ | bm_1_pd_count_ch3 | 11088
PD Channel 1 Average Number of Events per Cycle Without Discrimination | BMT | 0 - 4294967295 |  | 11095 | FLOAT32 | 1 |  | 30 | 10048 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdCntN1 |  | mag | f | BMT/SPDC1$MX$PdCntN1$mag$f | ✔ | bm_1_pd_count_ch1_nless | 11096
PD Channel 2 Average Number of Events per Cycle Without Discrimination | BMT | 0 - 4294967295 |  | 11097 | FLOAT32 | 1 |  | 30 | 10049 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdCntN2 |  | mag | f | BMT/SPDC1$MX$PdCntN2$mag$f | ✔ | bm_1_pd_count_ch2_nless | 11098
PD Channel 3 Average Number of Events per Cycle Without Discrimination | BMT | 0 - 4294967295 |  | 11099 | FLOAT32 | 1 |  | 30 | 10050 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdCntN3 |  | mag | f | BMT/SPDC1$MX$PdCntN3$mag$f | ✔ | bm_1_pd_count_ch3_nless | 11100
PD Channel 1 Average Charge (pC) | BMT | 0 - 4294967295 pC |  | 11101 | FLOAT32 | 1 |  | 30 | 10051 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdVal1 |  | mag | f | BMT/SPDC1$MX$PdVal1$mag$f | ✔ | bm_1_pd_value_ch1 | 11102
PD Channel 2 Average Charge (pC) | BMT | 0 - 4294967295 pC |  | 11103 | FLOAT32 | 1 |  | 30 | 10052 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdVal2 |  | mag | f | BMT/SPDC1$MX$PdVal2$mag$f | ✔ | bm_1_pd_value_ch2 | 11104
PD Channel 3 Average Charge (pC) | BMT | 0 - 4294967295 pC |  | 11105 | FLOAT32 | 1 |  | 30 | 10053 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdVal3 |  | mag | f | BMT/SPDC1$MX$PdVal3$mag$f | ✔ | bm_1_pd_value_ch3 | 11106
PD Channel 1 Average Charge Without Discrimination (pC) | BMT | 0 - 4294967295 pC |  | 11113 | FLOAT32 | 1 |  | 30 | 10057 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdValN1 |  | mag | f | BMT/SPDC1$MX$PdValN1$mag$f | ✔ | bm_1_pd_value_ch1_nless | 11114
PD Channel 2 Average Charge Without Discrimination (pC) | BMT | 0 - 4294967295 pC |  | 11115 | FLOAT32 | 1 |  | 30 | 10058 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdValN2 |  | mag | f | BMT/SPDC1$MX$PdValN2$mag$f | ✔ | bm_1_pd_value_ch2_nless | 11116
PD Channel 3 Average Charge Without Discrimination (pC) | BMT | 0 - 4294967295 pC |  | 11117 | FLOAT32 | 1 |  | 30 | 10059 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdValN3 |  | mag | f | BMT/SPDC1$MX$PdValN3$mag$f | ✔ | bm_1_pd_value_ch3_nless | 11118
PD Channel 1 Maximum Value since last reporting (pC) | BMT | 0 - 4294967295 pC |  | 11119 | FLOAT32 | 1 |  | 30 | 10060 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdMax1 |  | mag | f | BMT/SPDC1$MX$PdMax1$mag$f | ✔ | bm_1_pd_max_ch1 | 11120
PD Channel 2 Maximum Value since last reporting (pC) | BMT | 0 - 4294967295 pC |  | 11121 | FLOAT32 | 1 |  | 30 | 10061 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdMax2 |  | mag | f | BMT/SPDC1$MX$PdMax2$mag$f | ✔ | bm_1_pd_max_ch2 | 11122
PD Channel 3 Maximum Value since last reporting (pC) | BMT | 0 - 4294967295 pC |  | 11123 | FLOAT32 | 1 |  | 30 | 10062 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdMax3 |  | mag | f | BMT/SPDC1$MX$PdMax3$mag$f | ✔ | bm_1_pd_max_ch3 | 11124
PD Channel 1 Maximum Value since last reporting Without Discrimination (pC) | BMT | 0 - 4294967295 pC |  | 11131 | FLOAT32 | 1 |  | 30 | 10066 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdMaxN1 |  | mag | f | BMT/SPDC1$MX$PdMaxN1$mag$f | ✔ | bm_1_pd_max_ch1_nless | 11132
PD Channel 2 Maximum Value since last reporting Without Discrimination (pC) | BMT | 0 - 4294967295 pC |  | 11133 | FLOAT32 | 1 |  | 30 | 10067 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdMaxN2 |  | mag | f | BMT/SPDC1$MX$PdMaxN2$mag$f | ✔ | bm_1_pd_max_ch2_nless | 11134
PD Channel 3 Maximum Value since last reporting Without Discrimination (pC) | BMT | 0 - 4294967295 pC |  | 11135 | FLOAT32 | 1 |  | 30 | 10068 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdMaxN3 |  | mag | f | BMT/SPDC1$MX$PdMaxN3$mag$f | ✔ | bm_1_pd_max_ch3_nless | 11136
PD Channel 1 Measured Noise Threshold Level | BMT | 0 - 65535 |  | 11137 | FLOAT32 | 1 |  | 30 | 10069 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | Noise1 |  | mag | f | BMT/SPDC1$MX$Noise1$mag$f | ✔ | bm_1_hf_noise_ch1 | 11138
PD Channel 2 Measured Noise Threshold Level | BMT | 0 - 65535 |  | 11139 | FLOAT32 | 1 |  | 30 | 10070 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | Noise2 |  | mag | f | BMT/SPDC1$MX$Noise2$mag$f | ✔ | bm_1_hf_noise_ch2 | 11140
PD Channel 3 Measured Noise Threshold Level | BMT | 0 - 65535 |  | 11141 | FLOAT32 | 1 |  | 30 | 10071 | 2 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | Noise3 |  | mag | f | BMT/SPDC1$MX$Noise3$mag$f | ✔ | bm_1_hf_noise_ch3 | 11142
BM Ambient Temperature (°C) | BMT | -32768 - 32767 |  | 11149 | FLOAT32 | 1 |  | 30 | 10075 | 2 | 5 | 7 | ✔ | Active |  | BMT | TTMP1 | MX | Tmp5 |  | instMag | f | BMT/TTMP1$MX$Tmp5$instMag$f | ✔ | bm_1_ambient_temperature | 11150
BM Ambient Relative Humidity (%) | BMT | 0-100 % |  | 11151 | FLOAT32 | 1 |  | 30 | 10076 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Hum |  | mag | f | BMT/GGIO2$MX$Hum$mag$f | ✔ | bm_1_ambient_humidity | 11152
BM Top Oil Temperature sensor 1 (°C) | BMT | -32768 - 32767 °C |  | 11153 | FLOAT32 | 1 |  | 30 | 10077 | 2 | 5 | 7 | ✔ | Active |  | BMT | TTMP1 | MX | Tmp1 |  | instMag | f | BMT/TTMP1$MX$Tmp1$instMag$f | ✔ | bm_1_top_oil1 | 11154
BM Top Oil Temperature sensor 2 (°C) | BMT | -32768 - 32767 °C |  | 11155 | FLOAT32 | 1 |  | 30 | 10078 | 2 | 5 | 7 | ✔ | Active |  | BMT | TTMP1 | MX | Tmp2 |  | instMag | f | BMT/TTMP1$MX$Tmp2$instMag$f | ✔ | bm_1_top_oil2 | 11156
BM Top Oil Temperature sensor 3 (°C) | BMT | -32768 - 32767 °C |  | 11157 | FLOAT32 | 1 |  | 30 | 10079 | 2 | 5 | 7 | ✔ | Active |  | BMT | TTMP1 | MX | Tmp3 |  | instMag | f | BMT/TTMP1$MX$Tmp3$instMag$f | ✔ | bm_1_top_oil3 | 11158
BM Top Oil Temperature sensor 4 (°C) | BMT | -32768 - 32767 °C |  | 11159 | FLOAT32 | 1 |  | 30 | 10080 | 2 | 5 | 7 | ✔ | Active |  | BMT | TTMP1 | MX | Tmp4 |  | instMag | f | BMT/TTMP1$MX$Tmp4$instMag$f | ✔ | bm_1_top_oil4 | 11160
BM Set1 FPGA temeprature | BMT | -32768 - 32767 °C |  | 11161 | FLOAT32 | 1 |  | 30 | 10081 | 2 | 5 | 7 | ✔ | Disabled |  | BMT | TTMP1 | MX | Tmp6 |  | instMag | f | BMT/TTMP1$MX$Tmp6$instMag$f | ✔ | bm_1_fpga_temp | 11162
BM Set1 FPGA power supplier temperature | BMT | -32768 - 32767 °C |  | 11163 | FLOAT32 | 1 |  | 30 | 10082 | 2 | 5 | 7 | ✔ | Disabled |  | BMT | TTMP1 | MX | Tmp7 |  | instMag | f | BMT/TTMP1$MX$Tmp7$instMag$f | ✔ | bm_1_fpga_psu_temp | 11164
BM Set1 Internal CPU temperature | BMT | -32768 - 32767 °C |  | 11165 | FLOAT32 | 1 |  | 30 | 10083 | 2 | 5 | 7 | ✔ | Disabled |  | BMT | TTMP1 | MX | Tmp8 |  | instMag | f | BMT/TTMP1$MX$Tmp8$instMag$f | ✔ | bm_1_cpu_temp | 11166
BM Phase Angle Delta Channels 1-2 | BMT | -180 - 180 |  | 11185 | FLOAT32 | 1 |  | 30 | 10093 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Phd12 |  | mag | f | BMT/GGIO2$MX$Phd12$mag$f | ✔ | bo_1_delta_angle_ch12 | 11186
BM Phase Angle Delta Channels 1-3 | BMT | -180 - 180 |  | 11187 | FLOAT32 | 1 |  | 30 | 10094 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Phd13 |  | mag | f | BMT/GGIO2$MX$Phd13$mag$f | ✔ | bo_1_delta_angle_ch13 | 11188
BM Phase Angle Delta Channels 4-5 | BMT | -180 - 180 |  | 11189 | FLOAT32 | 1 |  | 30 | 10095 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Phd45 |  | mag | f | BMT/GGIO2$MX$Phd45$mag$f | ✔ | bo_1_delta_angle_ch45 | 11190
BM Phase Angle Delta Channels 4-6 | BMT | -180 - 180 |  | 11191 | FLOAT32 | 1 |  | 30 | 10096 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Phd46 |  | mag | f | BMT/GGIO2$MX$Phd46$mag$f | ✔ | bo_1_delta_angle_ch46 | 11192
BM Channel 1 Estimated C1 | BMT | 0 - 4294967295 |  | 11199 | FLOAT32 | 1 |  | 30 | 10100 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | React1 |  | mag | f | BMT/GGIO2$MX$React1$mag$f | ✔ | bm_1_c1_est_ch1 | 11200
BM Channel 2 Estimated C1 | BMT | 0 - 4294967295 |  | 11201 | FLOAT32 | 1 |  | 30 | 10101 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | React2 |  | mag | f | BMT/GGIO2$MX$React2$mag$f | ✔ | bm_1_c1_est_ch2 | 11202
BM Channel 3 Estimated C1 | BMT | 0 - 4294967295 |  | 11203 | FLOAT32 | 1 |  | 30 | 10102 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | React3 |  | mag | f | BMT/GGIO2$MX$React3$mag$f | ✔ | bm_1_c1_est_ch3 | 11204
BM Channel 4 Estimated C1 | BMT | 0 - 4294967295 |  | 11205 | FLOAT32 | 1 |  | 30 | 10103 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | React4 |  | mag | f | BMT/GGIO2$MX$React4$mag$f | ✔ | bm_1_c1_est_ch4 | 11206
BM Channel 5 Estimated C1 | BMT | 0 - 4294967295 |  | 11207 | FLOAT32 | 1 |  | 30 | 10104 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | React5 |  | mag | f | BMT/GGIO2$MX$React5$mag$f | ✔ | bm_1_c1_est_ch5 | 11208
BM Channel 6 Estimated C1 | BMT | 0 - 4294967295 |  | 11209 | FLOAT32 | 1 |  | 30 | 10105 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | React6 |  | mag | f | BMT/GGIO2$MX$React6$mag$f | ✔ | bm_1_c1_est_ch6 | 11210
BM Channel 7 Estimated C1 | BMT | 0 - 4294967295 |  | 11211 | FLOAT32 | 1 |  | 30 | 10106 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | React1 |  | mag | f | BMT/GGIO3$MX$React1$mag$f | ✔ | bm_2_c1_est_ch1 | 11212
BM Channel 8 Estimated C1 | BMT | 0 - 4294967295 |  | 11213 | FLOAT32 | 1 |  | 30 | 10107 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | React2 |  | mag | f | BMT/GGIO3$MX$React2$mag$f | ✔ | bm_2_c1_est_ch2 | 11214
BM Channel 9 Estimated C1 | BMT | 0 - 4294967295 |  | 11215 | FLOAT32 | 1 |  | 30 | 10108 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | React3 |  | mag | f | BMT/GGIO3$MX$React3$mag$f | ✔ | bm_2_c1_est_ch3 | 11216
BM Set2 Power Frequency (Hz) | BMT | 45-65 Hz |  | 11217 | FLOAT32 | 1 |  | 30 | 10109 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | Frequency |  | mag | f | BMT/GGIO3$MX$Frequency$mag$f | ✔ | bm_2_frequency | 11218
BM Channel 7 Bushing Current | BMT | 0 - 4294967295 A |  | 11225 | FLOAT32 | 1 |  | 30 | 10113 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | LeakA1 |  | mag | f | BMT/ZBSH2$MX$LeakA1$mag$f | ✔ | bm_2_current_ch1 | 11226
BM Channel 8 Bushing Current | BMT | 0 - 4294967295 A |  | 11227 | FLOAT32 | 1 |  | 30 | 10114 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | LeakA2 |  | mag | f | BMT/ZBSH2$MX$LeakA2$mag$f | ✔ | bm_2_current_ch2 | 11228
BM Channel 9 Bushing Current | BMT | 0 - 4294967295 A |  | 11229 | FLOAT32 | 1 |  | 30 | 10115 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | LeakA3 |  | mag | f | BMT/ZBSH2$MX$LeakA3$mag$f | ✔ | bm_2_current_ch3 | 11230
BM Channel 7 Estimated ΔC1 | BMT | 0 - 4294967295 |  | 11231 | FLOAT32 | 1 |  | 30 | 10116 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | React1 |  | mag | f | BMT/ZBSH2$MX$React1$mag$f | ✔ | bm_2_c1_ch1 | 11232
BM Channel 8 Estimated ΔC1 | BMT | 0 - 4294967295 |  | 11233 | FLOAT32 | 1 |  | 30 | 10117 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | React2 |  | mag | f | BMT/ZBSH2$MX$React2$mag$f | ✔ | bm_2_c1_ch2 | 11234
BM Channel 9 Estimated ΔC1 | BMT | 0 - 4294967295 |  | 11235 | FLOAT32 | 1 |  | 30 | 10118 | 2 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | React3 |  | mag | f | BMT/ZBSH2$MX$React3$mag$f | ✔ | bm_2_c1_ch3 | 11236
BM Phase Angle Channels 7-8 | BMT | -180 - 180 |  | 11237 | FLOAT32 | 1 |  | 30 | 10119 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | Phs12 |  | mag | f | BMT/GGIO3$MX$Phs12$mag$f | ✔ | bm_2_angle_ch12 | 11238
BM Phase Angle Channels 7-9 | BMT | -180 - 180 |  | 11239 | FLOAT32 | 1 |  | 30 | 10120 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | Phs13 |  | mag | f | BMT/GGIO3$MX$Phs13$mag$f | ✔ | bm_2_angle_ch13 | 11240
BM Set2 FPGA temeprature | BMT | -32768 - 32767 °C |  | 11265 | FLOAT32 | 1 |  | 30 | 10133 | 2 | 5 | 7 | ✔ | Active |  | BMT | TTMP1 | MX | Tmp9 |  | instMag | f | BMT/TTMP1$MX$Tmp9$instMag$f | ✔ | bm_2_fpga_temp | 11266
BM Set2 FPGA power supplier temperature | BMT | -32768 - 32767 °C |  | 11267 | FLOAT32 | 1 |  | 30 | 10134 | 2 | 5 | 7 | ✔ | Active |  | BMT | TTMP1 | MX | Tmp10 |  | instMag | f | BMT/TTMP1$MX$Tmp10$instMag$f | ✔ | bm_2_fpga_psu_temp | 11268
BM Set2 Internal CPU temperature | BMT | -32768 - 32767 °C |  | 11269 | FLOAT32 | 1 |  | 30 | 10135 | 2 | 5 | 7 | ✔ | Active |  | BMT | TTMP1 | MX | Tmp11 |  | instMag | f | BMT/TTMP1$MX$Tmp11$instMag$f | ✔ | bm_2_cpu_temp | 11270
BM Phase Angle Delta Channels 7-8 | BMT | -180 - 180 |  | 11271 | FLOAT32 | 1 |  | 30 | 10136 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | Phd12 |  | mag | f | BMT/GGIO3$MX$Phd12$mag$f | ✔ | bo_2_delta_angle_ch12 | 11272
BM Phase Angle Delta Channels 7-9 | BMT | -180 - 180 |  | 11273 | FLOAT32 | 1 |  | 30 | 10137 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | Phd13 |  | mag | f | BMT/GGIO3$MX$Phd13$mag$f | ✔ | bo_2_delta_angle_ch13 | 11274
BM Set 1 Polar Plot C1% | BMT | 0-100% |  | 11275 | FLOAT32 | 1 |  | 30 | 10138 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | ReactP |  | mag | f | BMT/GGIO2$MX$ReactP$mag$f | ✔ | bo_1_c1_primary_modulo | 11276
BM Set 1 Polar Plot PF% | BMT | 0-1000% |  | 11277 | FLOAT32 | 1 |  | 30 | 10139 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | LosFactP |  | mag | f | BMT/GGIO2$MX$LosFactP$mag$f | ✔ | bo_1_pf_primary_modulo | 11278
BM Set 2 Polar Plot C1% | BMT | 0-100% |  | 11279 | FLOAT32 | 1 |  | 30 | 10140 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | ReactS |  | mag | f | BMT/GGIO2$MX$ReactS$mag$f | ✔ | bo_1_c1_secondary_modulo | 11280
BM Set 2 Polar Plot PF% | BMT | 0-1000% |  | 11281 | FLOAT32 | 1 |  | 30 | 10141 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | LosFactS |  | mag | f | BMT/GGIO2$MX$LosFactS$mag$f | ✔ | bo_1_pf_secondary_modulo | 11282
BM Set 3 Polar Plot C1% | BMT | 0-100% |  | 11283 | FLOAT32 | 1 |  | 30 | 10142 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | ReactP |  | mag | f | BMT/GGIO3$MX$ReactP$mag$f | ✔ | bo_2_c1_primary_modulo | 11284
BM Set 3 Polar Plot PF% | BMT | 0-1000% |  | 11285 | FLOAT32 | 1 |  | 30 | 10143 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | LosFactP |  | mag | f | BMT/GGIO3$MX$LosFactP$mag$f | ✔ | bo_2_pf_primary_modulo | 11286
BM 4-20mA Top Oil Temperature Sensor 1 (°C) (Mapped to AIN) | BMT | -32768 - 32767 °C |  | 11287 | FLOAT33 | 2 |  | 30 | 10144 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Tmp1 |  | mag | f | BMT/GGIO2$MX$Tmp1$mag$f | ✔ | bm_1_ain_top_oil1_est | 11288
BM 4-20mA Top Oil Temperature Sensor 2 (°C) (Mapped to AIN) | BMT | -32768 - 32767 °C |  | 11289 | FLOAT34 | 3 |  | 30 | 10145 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Tmp2 |  | mag | f | BMT/GGIO2$MX$Tmp2$mag$f | ✔ | bm_1_ain_top_oil2_est | 11290
BM 4-20mA Top Oil Temperature Sensor 3 (°C) (Mapped to AIN) | BMT | -32768 - 32767 °C |  | 11291 | FLOAT35 | 4 |  | 30 | 10146 | 2 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Tmp3 |  | mag | f | BMT/GGIO2$MX$Tmp3$mag$f | ✔ | bm_1_ain_top_oil3_est | 11292
BM Channel 1 C1 High-High Alarm Limit | BMT | 0 - 50 |  | 11299 | FLOAT32 | 1 |  | 30 | 10300 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React1AlsH |  | mag | f | BMT/ZBSH1$MX$React1AlsH$mag$f | ✔ | bm_1_c1_ch1__high_high__limit | 11300
BM Channel 1 C1 High Alarm Limit | BMT | 0 - 50 |  | 11301 | FLOAT32 | 1 |  | 30 | 10301 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React1WrsH |  | mag | f | BMT/ZBSH1$MX$React1WrsH$mag$f | ✔ | bm_1_c1_ch1__high__limit | 11302
BM Channel 1 C1 Low Alarm Limit | BMT | 0 - 50 |  | 11303 | FLOAT32 | 1 |  | 30 | 10302 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React1WrsL |  | mag | f | BMT/ZBSH1$MX$React1WrsL$mag$f | ✔ | bm_1_c1_ch1__low__limit | 11304
BM Channel 1 C1 Low-Low Alarm Limit | BMT | 0 - 50 |  | 11305 | FLOAT32 | 1 |  | 30 | 10303 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React1AlsL |  | mag | f | BMT/ZBSH1$MX$React1AlsL$mag$f | ✔ | bm_1_c1_ch1__low_low__limit | 11306
BM Channel 2 C1 High-High Alarm Limit | BMT | 0 - 50 |  | 11307 | FLOAT32 | 1 |  | 30 | 10304 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React2AlsH |  | mag | f | BMT/ZBSH1$MX$React2AlsH$mag$f | ✔ | bm_1_c1_ch2__high_high__limit | 11308
BM Channel 2 C1 High Alarm Limit | BMT | 0 - 50 |  | 11309 | FLOAT32 | 1 |  | 30 | 10305 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React2WrsH |  | mag | f | BMT/ZBSH1$MX$React2WrsH$mag$f | ✔ | bm_1_c1_ch2__high__limit | 11310
BM Channel 2 C1 Low Alarm Limit | BMT | 0 - 50 |  | 11311 | FLOAT32 | 1 |  | 30 | 10306 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React2WrsL |  | mag | f | BMT/ZBSH1$MX$React2WrsL$mag$f | ✔ | bm_1_c1_ch2__low__limit | 11312
BM Channel 2 C1 Low-Low Alarm Limit | BMT | 0 - 50 |  | 11313 | FLOAT32 | 1 |  | 30 | 10307 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React2AlsL |  | mag | f | BMT/ZBSH1$MX$React2AlsL$mag$f | ✔ | bm_1_c1_ch2__low_low__limit | 11314
BM Channel 3 C1 High-High Alarm Limit | BMT | 0 - 50 |  | 11315 | FLOAT32 | 1 |  | 30 | 10308 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React3AlsH |  | mag | f | BMT/ZBSH1$MX$React3AlsH$mag$f | ✔ | bm_1_c1_ch3__high_high__limit | 11316
BM Channel 3 C1 High Alarm Limit | BMT | 0 - 50 |  | 11317 | FLOAT32 | 1 |  | 30 | 10309 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React3WrsH |  | mag | f | BMT/ZBSH1$MX$React3WrsH$mag$f | ✔ | bm_1_c1_ch3__high__limit | 11318
BM Channel 3 C1 Low Alarm Limit | BMT | 0 - 50 |  | 11319 | FLOAT32 | 1 |  | 30 | 10310 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React3WrsL |  | mag | f | BMT/ZBSH1$MX$React3WrsL$mag$f | ✔ | bm_1_c1_ch3__low__limit | 11320
BM Channel 3 C1 Low-Low Alarm Limit | BMT | 0 - 50 |  | 11321 | FLOAT32 | 1 |  | 30 | 10311 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React3AlsL |  | mag | f | BMT/ZBSH1$MX$React3AlsL$mag$f | ✔ | bm_1_c1_ch3__low_low__limit | 11322
BM Channel 4 C1 High-High Alarm Limit | BMT | 0 - 50 |  | 11323 | FLOAT32 | 1 |  | 30 | 10312 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React4AlsH |  | mag | f | BMT/ZBSH1$MX$React4AlsH$mag$f | ✔ | bm_1_c1_ch4__high_high__limit | 11324
BM Channel 4 C1 High Alarm Limit | BMT | 0 - 50 |  | 11325 | FLOAT32 | 1 |  | 30 | 10313 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React4WrsH |  | mag | f | BMT/ZBSH1$MX$React4WrsH$mag$f | ✔ | bm_1_c1_ch4__high__limit | 11326
BM Channel 4 C1 Low Alarm Limit | BMT | 0 - 50 |  | 11327 | FLOAT32 | 1 |  | 30 | 10314 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React4WrsL |  | mag | f | BMT/ZBSH1$MX$React4WrsL$mag$f | ✔ | bm_1_c1_ch4__low__limit | 11328
BM Channel 4 C1 Low-Low Alarm Limit | BMT | 0 - 50 |  | 11329 | FLOAT32 | 1 |  | 30 | 10315 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React4AlsL |  | mag | f | BMT/ZBSH1$MX$React4AlsL$mag$f | ✔ | bm_1_c1_ch4__low_low__limit | 11330
BM Channel 5 C1 High-High Alarm Limit | BMT | 0 - 50 |  | 11331 | FLOAT32 | 1 |  | 30 | 10316 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React5AlsH |  | mag | f | BMT/ZBSH1$MX$React5AlsH$mag$f | ✔ | bm_1_c1_ch5__high_high__limit | 11332
BM Channel 5 C1 High Alarm Limit | BMT | 0 - 50 |  | 11333 | FLOAT32 | 1 |  | 30 | 10317 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React5WrsH |  | mag | f | BMT/ZBSH1$MX$React5WrsH$mag$f | ✔ | bm_1_c1_ch5__high__limit | 11334
BM Channel 5 C1 Low Alarm Limit | BMT | 0 - 50 |  | 11335 | FLOAT32 | 1 |  | 30 | 10318 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React5WrsL |  | mag | f | BMT/ZBSH1$MX$React5WrsL$mag$f | ✔ | bm_1_c1_ch5__low__limit | 11336
BM Channel 5 C1 Low-Low Alarm Limit | BMT | 0 - 50 |  | 11337 | FLOAT32 | 1 |  | 30 | 10319 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React5AlsL |  | mag | f | BMT/ZBSH1$MX$React5AlsL$mag$f | ✔ | bm_1_c1_ch5__low_low__limit | 11338
BM Channel 6 C1 High-High Alarm Limit | BMT | 0 - 50 |  | 11339 | FLOAT32 | 1 |  | 30 | 10320 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React6AlsH |  | mag | f | BMT/ZBSH1$MX$React6AlsH$mag$f | ✔ | bm_1_c1_ch6__high_high__limit | 11340
BM Channel 6 C1 High Alarm Limit | BMT | 0 - 50 |  | 11341 | FLOAT32 | 1 |  | 30 | 10321 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React6WrsH |  | mag | f | BMT/ZBSH1$MX$React6WrsH$mag$f | ✔ | bm_1_c1_ch6__high__limit | 11342
BM Channel 6 C1 Low Alarm Limit | BMT | 0 - 50 |  | 11343 | FLOAT32 | 1 |  | 30 | 10322 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React6WrsL |  | mag | f | BMT/ZBSH1$MX$React6WrsL$mag$f | ✔ | bm_1_c1_ch6__low__limit | 11344
BM Channel 6 C1 Low-Low Alarm Limit | BMT | 0 - 50 |  | 11345 | FLOAT32 | 1 |  | 30 | 10323 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH1 | MX | React6AlsL |  | mag | f | BMT/ZBSH1$MX$React6AlsL$mag$f | ✔ | bm_1_c1_ch6__low_low__limit | 11346
BM Phase Angle Delta Channels 1-2 High-High Alarm Limit | BMT | 0.2 - 3 |  | 11347 | FLOAT32 | 1 |  | 30 | 10324 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Phd12AlsH |  | mag | f | BMT/GGIO2$MX$Phd12AlsH$mag$f | ✔ | bo_1_delta_angle_ch12__high_high__limit | 11348
BM Phase Angle Delta Channels 1-2 High Alarm Limit | BMT | 0.2 - 3 |  | 11349 | FLOAT32 | 1 |  | 30 | 10325 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Phd12WrsH |  | mag | f | BMT/GGIO2$MX$Phd12WrsH$mag$f | ✔ | bo_1_delta_angle_ch12__high__limit | 11350
BM Phase Angle Delta Channels 1-3 High-High Alarm Limit | BMT | 0.2 - 3 |  | 11351 | FLOAT32 | 1 |  | 30 | 10326 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Phd13AlsH |  | mag | f | BMT/GGIO2$MX$Phd13AlsH$mag$f | ✔ | bo_1_delta_angle_ch13__high_high__limit | 11352
BM Phase Angle Delta Channels 1-3 High Alarm Limit | BMT | 0.2 - 3 |  | 11353 | FLOAT32 | 1 |  | 30 | 10327 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Phd13WrsH |  | mag | f | BMT/GGIO2$MX$Phd13WrsH$mag$f | ✔ | bo_1_delta_angle_ch13__high__limit | 11354
BM Phase Angle Delta Channels 4-5 High-High Alarm Limit | BMT | 0.2 - 3 |  | 11355 | FLOAT32 | 1 |  | 30 | 10328 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Phd45AlsH |  | mag | f | BMT/GGIO2$MX$Phd45AlsH$mag$f | ✔ | bo_1_delta_angle_ch45__high_high__limit | 11356
BM Phase Angle Delta Channels 4-5 High Alarm Limit | BMT | 0.2 - 3 |  | 11357 | FLOAT32 | 1 |  | 30 | 10329 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Phd45WrsH |  | mag | f | BMT/GGIO2$MX$Phd45WrsH$mag$f | ✔ | bo_1_delta_angle_ch45__high__limit | 11358
BM Phase Angle Delta Channels 4-6 High-High Alarm Limit | BMT | 0.2 - 3 |  | 11359 | FLOAT32 | 1 |  | 30 | 10330 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Phd46AlsH |  | mag | f | BMT/GGIO2$MX$Phd46AlsH$mag$f | ✔ | bo_1_delta_angle_ch46__high_high__limit | 11360
BM Phase Angle Delta Channels 4-6 High Alarm Limit | BMT | 0.2 - 3 |  | 11361 | FLOAT32 | 1 |  | 30 | 10331 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | Phd46WrsH |  | mag | f | BMT/GGIO2$MX$Phd46WrsH$mag$f | ✔ | bo_1_delta_angle_ch46__high__limit | 11362
PD Channel 1 Maximum Value High-High Alarm Limit (pC) | BMT | 1000 - 65535 pC |  | 11363 | FLOAT32 | 1 |  | 30 | 10332 | 3 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdMax1AlsH |  | mag | f | BMT/SPDC1$MX$PdMax1AlsH$mag$f | ✔ | bm_1_pd_max_ch1__high_high__limit | 11364
PD Channel 1 Maximum Value High Alarm Limit (pC) | BMT | 1000 - 65535 pC |  | 11365 | FLOAT32 | 1 |  | 30 | 10333 | 3 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdMax1WrsH |  | mag | f | BMT/SPDC1$MX$PdMax1WrsH$mag$f | ✔ | bm_1_pd_max_ch1__high__limit | 11366
PD Channel 2 Maximum Value High-High Alarm Limit (pC) | BMT | 1000 - 65535 pC |  | 11367 | FLOAT32 | 1 |  | 30 | 10334 | 3 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdMax2AlsH |  | mag | f | BMT/SPDC1$MX$PdMax2AlsH$mag$f | ✔ | bm_1_pd_max_ch2__high_high__limit | 11368
PD Channel 2 Maximum Value High Alarm Limit (pC) | BMT | 1000 - 65535 pC |  | 11369 | FLOAT32 | 1 |  | 30 | 10335 | 3 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdMax2WrsH |  | mag | f | BMT/SPDC1$MX$PdMax2WrsH$mag$f | ✔ | bm_1_pd_max_ch2__high__limit | 11370
PD Channel 3 Maximum Value High-High Alarm Limit (pC) | BMT | 1000 - 65535 pC |  | 11371 | FLOAT32 | 1 |  | 30 | 10336 | 3 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdMax3AlsH |  | mag | f | BMT/SPDC1$MX$PdMax3AlsH$mag$f | ✔ | bm_1_pd_max_ch3__high_high__limit | 11372
PD Channel 3 Maximum Value High Alarm Limit (pC) | BMT | 1000 - 65535 pC |  | 11373 | FLOAT32 | 1 |  | 30 | 10337 | 3 | 5 | 7 | ✔ | Active |  | BMT | SPDC1 | MX | PdMax3WrsH |  | mag | f | BMT/SPDC1$MX$PdMax3WrsH$mag$f | ✔ | bm_1_pd_max_ch3__high__limit | 11374
BM Set 1 Polar Plot C1% High-High Alarm Limit | BMT | 1 - 25 |  | 11405 | FLOAT32 | 1 |  | 30 | 10353 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | ReactPAlsH |  | mag | f | BMT/GGIO2$MX$ReactPAlsH$mag$f | ✔ | bo_1_c1_primary_modulo__high_high__limit | 11406
BM Set 1 Polar Plot C1% High Alarm Limit | BMT | 1 - 25 |  | 11407 | FLOAT32 | 1 |  | 30 | 10354 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | ReactPWrsH |  | mag | f | BMT/GGIO2$MX$ReactPWrsH$mag$f | ✔ | bo_1_c1_primary_modulo__high__limit | 11408
BM Set 2 Polar Plot C1% High-High Alarm Limit | BMT | 1 - 25 |  | 11409 | FLOAT32 | 1 |  | 30 | 10355 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | ReactSAlsH |  | mag | f | BMT/GGIO2$MX$ReactSAlsH$mag$f | ✔ | bo_1_c1_secondary_modulo__high_high__limit | 11410
BM Set 2 Polar Plot C1% High Alarm Limit | BMT | 1 - 25 |  | 11411 | FLOAT32 | 1 |  | 30 | 10356 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | ReactSWrsH |  | mag | f | BMT/GGIO2$MX$ReactSWrsH$mag$f | ✔ | bo_1_c1_secondary_modulo__high__limit | 11412
BM Set 1 Polar Plot PF% High-High Alarm Limit | BMT | 100 - 1500 |  | 11413 | FLOAT32 | 1 |  | 30 | 10357 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | LosFactPAlsH |  | mag | f | BMT/GGIO2$MX$LosFactPAlsH$mag$f | ✔ | bo_1_pf_primary_modulo__high_high__limit | 11414
BM Set 1 Polar Plot PF% High Alarm Limit | BMT | 100 - 1500 |  | 11415 | FLOAT32 | 1 |  | 30 | 10358 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | LosFactPWrsH |  | mag | f | BMT/GGIO2$MX$LosFactPWrsH$mag$f | ✔ | bo_1_pf_primary_modulo__high__limit | 11416
BM Set 2 Polar Plot PF% High-High Alarm Limit | BMT | 100 - 1500 |  | 11417 | FLOAT32 | 1 |  | 30 | 10359 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | LosFactSAlsH |  | mag | f | BMT/GGIO2$MX$LosFactSAlsH$mag$f | ✔ | bo_1_pf_secondary_modulo__high_high__limit | 11418
BM Set 2 Polar Plot PF% High Alarm Limit | BMT | 100 - 1500 |  | 11419 | FLOAT32 | 1 |  | 30 | 10360 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | LosFactSWrsH |  | mag | f | BMT/GGIO2$MX$LosFactSWrsH$mag$f | ✔ | bo_1_pf_secondary_modulo__high__limit | 11420
PD Set1 PDI Polar Plot High-High Alarm Limit | BMT | 100 - 65535 |  | 11421 | FLOAT32 | 1 |  | 30 | 10361 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | PdIdxPAlsH |  | mag | f | BMT/GGIO2$MX$PdIdxPAlsH$mag$f | ✔ | bo_1_pdi_primary_modulo__high_high__limit | 11422
PD Set1 PDI Polar Plot High Alarm Limit | BMT | 100 - 65535 |  | 11423 | FLOAT32 | 1 |  | 30 | 10362 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | PdIdxPWrsH |  | mag | f | BMT/GGIO2$MX$PdIdxPWrsH$mag$f | ✔ | bo_1_pdi_primary_modulo__high__limit | 11424
PD Set1 Average Number of Events per Cycle Polar Plot High-High Alarm Limit | BMT | 1 - 200 |  | 11425 | FLOAT32 | 1 |  | 30 | 10363 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | PdCntPAlsH |  | mag | f | BMT/GGIO2$MX$PdCntPAlsH$mag$f | ✔ | bo_1_pd_count_primary_modulo__high_high__limit | 11426
PD Set1 Average Number of Events per Cycle Polar Plot High Alarm Limit | BMT | 1 - 200 |  | 11427 | FLOAT32 | 1 |  | 30 | 10364 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | PdCntPWrsH |  | mag | f | BMT/GGIO2$MX$PdCntPWrsH$mag$f | ✔ | bo_1_pd_count_primary_modulo__high__limit | 11428
PD Set1 Average Charge Polar Plot High-High Alarm Limit (pC) | BMT | 100 - 65535 |  | 11429 | FLOAT32 | 1 |  | 30 | 10365 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | PdValPAlsH |  | mag | f | BMT/GGIO2$MX$PdValPAlsH$mag$f | ✔ | bo_1_pd_value_primary_modulo__high_high__limit | 11430
PD Set1 Average Charge Polar Plot High Alarm Limit (pC) | BMT | 100 - 65535 |  | 11431 | FLOAT32 | 1 |  | 30 | 10366 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | PdValPWrsH |  | mag | f | BMT/GGIO2$MX$PdValPWrsH$mag$f | ✔ | bo_1_pd_value_primary_modulo__high__limit | 11432
BM Channel 7 C1 High-High Alarm Limit | BMT | 0 - 50 |  | 11441 | FLOAT32 | 1 |  | 30 | 10371 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | React1AlsH |  | mag | f | BMT/ZBSH2$MX$React1AlsH$mag$f | ✔ | bm_2_c1_ch1__high_high__limit | 11442
BM Channel 7 C1 High Alarm Limit | BMT | 0 - 50 |  | 11443 | FLOAT32 | 1 |  | 30 | 10372 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | React1WrsH |  | mag | f | BMT/ZBSH2$MX$React1WrsH$mag$f | ✔ | bm_2_c1_ch1__high__limit | 11444
BM Channel 7 C1 Low Alarm Limit | BMT | 0 - 50 |  | 11445 | FLOAT32 | 1 |  | 30 | 10373 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | React1WrsL |  | mag | f | BMT/ZBSH2$MX$React1WrsL$mag$f | ✔ | bm_2_c1_ch1__low__limit | 11446
BM Channel 7 C1 Low-Low Alarm Limit | BMT | 0 - 50 |  | 11447 | FLOAT32 | 1 |  | 30 | 10374 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | React1AlsL |  | mag | f | BMT/ZBSH2$MX$React1AlsL$mag$f | ✔ | bm_2_c1_ch1__low_low__limit | 11448
BM Channel 8 C1 High-High Alarm Limit | BMT | 0 - 50 |  | 11449 | FLOAT32 | 1 |  | 30 | 10375 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | React2AlsH |  | mag | f | BMT/ZBSH2$MX$React2AlsH$mag$f | ✔ | bm_2_c1_ch2__high_high__limit | 11450
BM Channel 8 C1 High Alarm Limit | BMT | 0 - 50 |  | 11451 | FLOAT32 | 1 |  | 30 | 10376 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | React2WrsH |  | mag | f | BMT/ZBSH2$MX$React2WrsH$mag$f | ✔ | bm_2_c1_ch2__high__limit | 11452
BM Channel 8 C1 Low Alarm Limit | BMT | 0 - 50 |  | 11453 | FLOAT32 | 1 |  | 30 | 10377 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | React2WrsL |  | mag | f | BMT/ZBSH2$MX$React2WrsL$mag$f | ✔ | bm_2_c1_ch2__low__limit | 11454
BM Channel 8 C1 Low-Low Alarm Limit | BMT | 0 - 50 |  | 11455 | FLOAT32 | 1 |  | 30 | 10378 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | React2AlsL |  | mag | f | BMT/ZBSH2$MX$React2AlsL$mag$f | ✔ | bm_2_c1_ch2__low_low__limit | 11456
BM Channel 9 C1 High-High Alarm Limit | BMT | 0 - 50 |  | 11457 | FLOAT32 | 1 |  | 30 | 10379 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | React3AlsH |  | mag | f | BMT/ZBSH2$MX$React3AlsH$mag$f | ✔ | bm_2_c1_ch3__high_high__limit | 11458
BM Channel 9 C1 High Alarm Limit | BMT | 0 - 50 |  | 11459 | FLOAT32 | 1 |  | 30 | 10380 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | React3WrsH |  | mag | f | BMT/ZBSH2$MX$React3WrsH$mag$f | ✔ | bm_2_c1_ch3__high__limit | 11460
BM Channel 9 C1 Low Alarm Limit | BMT | 0 - 50 |  | 11461 | FLOAT32 | 1 |  | 30 | 10381 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | React3WrsL |  | mag | f | BMT/ZBSH2$MX$React3WrsL$mag$f | ✔ | bm_2_c1_ch3__low__limit | 11462
BM Channel 9 C1 Low-Low Alarm Limit | BMT | 0 - 50 |  | 11463 | FLOAT32 | 1 |  | 30 | 10382 | 3 | 5 | 7 | ✔ | Active |  | BMT | ZBSH2 | MX | React3AlsL |  | mag | f | BMT/ZBSH2$MX$React3AlsL$mag$f | ✔ | bm_2_c1_ch3__low_low__limit | 11464
BM Phase Angle Delta Channels 7-8 High-High Alarm Limit | BMT | 0.2 - 3 |  | 11465 | FLOAT32 | 1 |  | 30 | 10383 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | Phd12AlsH |  | mag | f | BMT/GGIO3$MX$Phd12AlsH$mag$f | ✔ | bo_2_delta_angle_ch12__high_high__limit | 11466
BM Phase Angle Delta Channels 7-8 High Alarm Limit | BMT | 0.2 - 3 |  | 11467 | FLOAT32 | 1 |  | 30 | 10384 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | Phd12WrsH |  | mag | f | BMT/GGIO3$MX$Phd12WrsH$mag$f | ✔ | bo_2_delta_angle_ch12__high__limit | 11468
BM Phase Angle Delta Channels 7-9 High-High Alarm Limit | BMT | 0.2 - 3 |  | 11469 | FLOAT32 | 1 |  | 30 | 10385 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | Phd13AlsH |  | mag | f | BMT/GGIO3$MX$Phd13AlsH$mag$f | ✔ | bo_2_delta_angle_ch13__high_high__limit | 11470
BM Phase Angle Delta Channels 7-9 High Alarm Limit | BMT | 0.2 - 3 |  | 11471 | FLOAT32 | 1 |  | 30 | 10386 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | Phd13WrsH |  | mag | f | BMT/GGIO3$MX$Phd13WrsH$mag$f | ✔ | bo_2_delta_angle_ch13__high__limit | 11472
BM Set 3 Polar Plot C1% High-High Alarm Limit | BMT | 1 - 25 |  | 11473 | FLOAT32 | 1 |  | 30 | 10387 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | ReactPAlsH |  | mag | f | BMT/GGIO3$MX$ReactPAlsH$mag$f | ✔ | bo_2_c1_primary_modulo__high_high__limit | 11474
BM Set 3 Polar Plot C1% High Alarm Limit | BMT | 1 - 25 |  | 11475 | FLOAT32 | 1 |  | 30 | 10388 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | ReactPWrsH |  | mag | f | BMT/GGIO3$MX$ReactPWrsH$mag$f | ✔ | bo_2_c1_primary_modulo__high__limit | 11476
BM Set 3 Polar Plot PF% High-High Alarm Limit | BMT | 100 - 1500 |  | 11477 | FLOAT32 | 1 |  | 30 | 10389 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | LosFactPAlsH |  | mag | f | BMT/GGIO3$MX$LosFactPAlsH$mag$f | ✔ | bo_2_pf_primary_modulo__high_high__limit | 11478
BM Set 3 Polar Plot PF% High Alarm Limit | BMT | 100 - 1500 |  | 11479 | FLOAT32 | 1 |  | 30 | 10390 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO3 | MX | LosFactPWrsH |  | mag | f | BMT/GGIO3$MX$LosFactPWrsH$mag$f | ✔ | bo_2_pf_primary_modulo__high__limit | 11480
BM Serial Number | BMT | N/A |  | 11549 | UINT32 | 1 |  | 30 | 10550 | 3 | 1 | 3 | ✔ | Active | [10 empty] | bp_1_serial_number | 11550
bh_1_device_id (characters 1-2) | BMT | N/A |  | 11599 | TEXT | N/A |  | 30 | 10600 | 3 | 4 | 2 | ✔ | Active | [10 empty] | bh_1_device_id (characters 1-2) | 11600
bh_1_device_id (characters 3-4) | BMT | N/A |  | 11600 | TEXT | N/A |  | 30 | 10601 | 3 | 4 | 2 | ✔ | Active | [10 empty] | bh_1_device_id (characters 3-4) | 11601
bh_1_device_id (characters 5-6) | BMT | N/A |  | 11601 | TEXT | N/A |  | 30 | 10602 | 3 | 4 | 2 | ✔ | Active | [10 empty] | bh_1_device_id (characters 5-6) | 11602
bh_1_device_id (characters 7-8) | BMT | N/A |  | 11602 | TEXT | N/A |  | 30 | 10603 | 3 | 4 | 2 | ✔ | Active | [10 empty] | bh_1_device_id (characters 7-8) | 11603
bh_1_device_id (characters 9-10) | BMT | N/A |  | 11603 | TEXT | N/A |  | 30 | 10604 | 3 | 4 | 2 | ✔ | Active | [10 empty] | bh_1_device_id (characters 9-10) | 11604
bh_1_device_id (characters 11-12) | BMT | N/A |  | 11604 | TEXT | N/A |  | 30 | 10605 | 3 | 4 | 2 | ✔ | Active | [10 empty] | bh_1_device_id (characters 11-12) | 11605
bh_1_device_id (characters 13-14) | BMT | N/A |  | 11605 | TEXT | N/A |  | 30 | 10606 | 3 | 4 | 2 | ✔ | Active | [10 empty] | bh_1_device_id (characters 13-14) | 11606
bh_1_device_id (characters 15-16) | BMT | N/A |  | 11606 | TEXT | N/A |  | 30 | 10607 | 3 | 4 | 2 | ✔ | Active | [10 empty] | bh_1_device_id (characters 15-16) | 11607
BM Top Oil Temperature sensor 1 (°C) High Alarm Limit | BMT | -32768 - 32767 °C |  | 11607 | FLOAT32 | 1 |  | 30 | 10608 | 3 | 5 | 7 | ✔ | Active |  | BMT | TTMP1 | MX | Tmp1Wrs |  | mag | f | BMT/TTMP1$MX$Tmp1Wrs$mag$f | ✔ | bm_1_top_oil1__high__limit | 11608
BM Top Oil Temperature sensor 2 (°C) High Alarm Limit | BMT | -32768 - 32767 °C |  | 11609 | FLOAT32 | 1 |  | 30 | 10609 | 3 | 5 | 7 | ✔ | Active |  | BMT | TTMP1 | MX | Tmp2Wrs |  | mag | f | BMT/TTMP1$MX$Tmp2Wrs$mag$f | ✔ | bm_1_top_oil2__high__limit | 11610
BM Top Oil Temperature sensor 3 (°C) High Alarm Limit | BMT | -32768 - 32767 °C |  | 11611 | FLOAT32 | 1 |  | 30 | 10610 | 3 | 5 | 7 | ✔ | Active |  | BMT | TTMP1 | MX | Tmp3Wrs |  | mag | f | BMT/TTMP1$MX$Tmp3Wrs$mag$f | ✔ | bm_1_top_oil3__high__limit | 11612
BM Top Oil Temperature sensor 4 (°C) High Alarm Limit | BMT | -32768 - 32767 °C |  | 11613 | FLOAT32 | 1 |  | 30 | 10611 | 3 | 5 | 7 | ✔ | Active |  | BMT | TTMP1 | MX | Tmp4Wrs |  | mag | f | BMT/TTMP1$MX$Tmp4Wrs$mag$f | ✔ | bm_1_top_oil4__high__limit | 11614
BM low signal threshold alarm limit | BMT | 0 - 4294967295 |  | 11615 | FLOAT32 | 1 |  | 30 | 10612 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | LowSigThd |  | mag | f | BMT/GGIO2$MX$LowSigThd$mag$f | ✔ | bs_1_low_current_threshold | 11616
BM over/under frequency alarm limit | BMT | 45-65 Hz |  | 11617 | FLOAT32 | 1 |  | 30 | 10613 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | FrqThd |  | mag | f | BMT/GGIO2$MX$FrqThd$mag$f | ✔ | bs_1_frequency_threshold | 11618
BM over/under frequency alarm hysteresis | BMT | 45-65 Hz |  | 11619 | FLOAT32 | 1 |  | 30 | 10614 | 3 | 5 | 7 | ✔ | Active |  | BMT | GGIO2 | MX | FrqHys |  | mag | f | BMT/GGIO2$MX$FrqHys$mag$f | ✔ | bs_1_frequency_threshold_hysteresis | 11620

## IEC61850 Datasets
Dataset Name | Description | Dataset Variables
ds_Mx_Gas_OS1 | Oil Source Dissolved Gas and Moisture Concentrations (ppm) | OS/SIML1$MX$H2ppm
OS/SIML1$MX$CO2ppm
OS/SIML1$MX$COppm
OS/SIML1$MX$C2H4ppm
OS/SIML1$MX$C2H6ppm
OS/SIML1$MX$CH4ppm
OS/SIML1$MX$C2H2ppm
OS/SIML1$MX$Mst
OS/SIML1$MX$O2ppm
OS/SIML1$MX$CmbuGas
OS/SIML1$MX$N2ppm
OS/SIML1$MX$FullGas
OS/SIML1$MX$HCGas
OS/SIML1$MX$CmbuLim
OS/SIML1$MX$Pres
OS/SIML1$MX$Tmp
OS/SIML1$MX$AmbTmp
OS/SIML1$MX$NorTmp
OS/SIML1$MX$H2O
OS/SIML1$MX$RCDCM
ds_Mx_GasRoC_OS1 | Oil Source Rate of change of Gas Concentrations (ppm/day) | OS/SIML1$MX$H2Rte
OS/SIML1$MX$CO2Rte
OS/SIML1$MX$CORte
OS/SIML1$MX$C2H4Rte
OS/SIML1$MX$C2H6Rte
OS/SIML1$MX$CH4Rte
OS/SIML1$MX$C2H2Rte
OS/SIML1$MX$MstRte
OS/SIML1$MX$O2Rte
OS/SIML1$MX$CgRte
OS/SIML1$MX$N2Rte
OS/SIML1$MX$RCDCMRte
OS/SIML1$MX$FullGasRte
OS/SIML1$MX$HCGasRte
OS/SIML1$MX$H2ORte
ds_St_Gas_OS1 | Oil Source Alarm Status of Gas Concentrations | OS/SIML1$ST$H2Alm
OS/SIML1$ST$H2Wrn
OS/SIML1$ST$CO2Alm
OS/SIML1$ST$CO2Wrn
OS/SIML1$ST$COAlm
OS/SIML1$ST$COWrn
OS/SIML1$ST$C2H4Alm
OS/SIML1$ST$C2H4Wrn
OS/SIML1$ST$C2H6Alm
OS/SIML1$ST$C2H6Wrn
OS/SIML1$ST$CH4Alm
OS/SIML1$ST$CH4Wrn
OS/SIML1$ST$C2H2Alm
OS/SIML1$ST$C2H2Wrn
OS/SIML1$ST$MstAlm
OS/SIML1$ST$MstWrn
OS/SIML1$ST$O2Alm
OS/SIML1$ST$O2Wrn
OS/SIML1$ST$CgAlm
OS/SIML1$ST$CgWrn
OS/SIML1$ST$N2Alm
OS/SIML1$ST$N2Wrn
OS/SIML1$ST$H2OAlm
OS/SIML1$ST$H2OWrn
ds_St_GasRoC_OS1 | Oil Source Alarm status of Rate of change of Gas Concentrations | OS/SIML1$ST$H2RteAlm
OS/SIML1$ST$H2RteWrn
OS/SIML1$ST$CO2RteAlm
OS/SIML1$ST$CO2RteWrn
OS/SIML1$ST$CORteAlm
OS/SIML1$ST$CORteWrn
OS/SIML1$ST$C2H4RteAlm
OS/SIML1$ST$C2H4RteWrn
OS/SIML1$ST$C2H6RteAlm
OS/SIML1$ST$C2H6RteWrn
OS/SIML1$ST$CH4RteAlm
OS/SIML1$ST$CH4RteWrn
OS/SIML1$ST$C2H2RteAlm
OS/SIML1$ST$C2H2RteWrn
OS/SIML1$ST$MstRteAlm
OS/SIML1$ST$MstRteWrn
OS/SIML1$ST$O2RteAlm
OS/SIML1$ST$O2RteWrn
OS/SIML1$ST$CgRteAlm
OS/SIML1$ST$CgRteWrn
OS/SIML1$ST$N2RteAlm
OS/SIML1$ST$N2RteWrn
ds_St_GasRatio_OS1 | Oil Source Alarm status of Ratios of Gas Concentration | OS/SIML1$ST$Rat1AlmH
OS/SIML1$ST$Rat1WrnH
OS/SIML1$ST$Rat1WrnL
OS/SIML1$ST$Rat1AlmL
OS/SIML1$ST$Rat2AlmH
OS/SIML1$ST$Rat2WrnH
OS/SIML1$ST$Rat2WrnL
OS/SIML1$ST$Rat2AlmL
OS/SIML1$ST$Rat3AlmH
OS/SIML1$ST$Rat3WrnH
OS/SIML1$ST$Rat3WrnL
OS/SIML1$ST$Rat3AlmL
OS/SIML1$ST$Rat4AlmH
OS/SIML1$ST$Rat4WrnH
OS/SIML1$ST$Rat4WrnL
OS/SIML1$ST$Rat4AlmL
OS/SIML1$ST$Rat5AlmH
OS/SIML1$ST$Rat5WrnH
OS/SIML1$ST$Rat5WrnL
OS/SIML1$ST$Rat5AlmL
OS/SIML1$ST$RCDCMAlmH
OS/SIML1$ST$RCDCMWrnH
OS/SIML1$ST$RCDCMWrnL
OS/SIML1$ST$RCDCMAlmL
OS/SIML1$ST$Rat6AlmH
OS/SIML1$ST$Rat6WrnH
OS/SIML1$ST$Rat6WrnL
OS/SIML1$ST$Rat6AlmL
OS/SIML1$ST$Rat7AlmH
OS/SIML1$ST$Rat7WrnH
OS/SIML1$ST$Rat7WrnL
OS/SIML1$ST$Rat7AlmL
ds_St_IO01 | Generic IO Alarms | OS/GGIO1$ST$Caution
OS/GGIO1$ST$Alarm
OS/GGIO1$ST$Service
OS/GGIO1$ST$Relay1
OS/GGIO1$ST$Relay2
OS/GGIO1$ST$Relay3
OS/GGIO1$ST$Relay4
OS/GGIO1$ST$Relay5
OS/GGIO1$ST$Relay6
OS/GGIO1$ST$Relay7
OS/GGIO1$ST$DiIn1
OS/GGIO1$ST$DiIn2
OS/GGIO1$ST$DiIn3
OS/GGIO1$ST$DiIn4
OS/GGIO1$ST$DiIn5
OS/GGIO1$ST$DiIn6
OS/GGIO1$ST$DiIn7
OS/GGIO1$ST$DiIn8
OS/GGIO1$ST$DiIn9
OS/GGIO1$ST$DiIn1Alm
OS/GGIO1$ST$DiIn2Alm
OS/GGIO1$ST$DiIn3Alm
OS/GGIO1$ST$DiIn4Alm
OS/GGIO1$ST$DiIn5Alm
OS/GGIO1$ST$DiIn6Alm
OS/GGIO1$ST$DiIn7Alm
OS/GGIO1$ST$DiIn8Alm
OS/GGIO1$ST$DiIn9Alm
ds_Mx_IO | Generic IO measurements | OS/GGIO1$MX$AnIn1
OS/GGIO1$MX$AnIn2
OS/GGIO1$MX$AnIn3
OS/GGIO1$MX$AnIn4
OS/GGIO1$MX$AnIn5
OS/GGIO1$MX$AnIn6
OS/GGIO1$ST$DiTr1
OS/GGIO1$ST$DiTr2
OS/GGIO1$ST$DiTr3
OS/GGIO1$ST$DiTr4
OS/GGIO1$ST$DiTr5
OS/GGIO1$ST$DiTr6
OS/GGIO1$ST$DiTr7
OS/GGIO1$ST$DiTr8
OS/GGIO1$ST$DiTr9
OS/GGIO1$MX$AnIn7
OS/GGIO1$MX$AnIn8
OS/GGIO1$MX$AnIn9
OS/GGIO1$MX$AnIn10
OS/GGIO1$MX$AnIn11
OS/GGIO1$MX$AnIn12
OS/GGIO1$MX$AnIn13
OS/GGIO1$MX$AnIn14
OS/GGIO1$MX$AnIn15
OS/GGIO1$MX$AnIn16
OS/GGIO1$MX$AnIn17
OS/GGIO1$MX$AnIn18
ds_Mx_TMP | TransOpto temperature measurements | OS/TTMP1$MX$Tmp1
OS/TTMP1$MX$Tmp2
OS/TTMP1$MX$Tmp3
OS/TTMP1$MX$Tmp4
OS/TTMP1$MX$Tmp5
OS/TTMP1$MX$Tmp6
OS/TTMP1$MX$Tmp7
OS/TTMP1$MX$Tmp8
OS/TTMP1$MX$TmpRte1
OS/TTMP1$MX$TmpRte2
OS/TTMP1$MX$TmpRte3
OS/TTMP1$MX$TmpRte4
OS/TTMP1$MX$TmpRte5
OS/TTMP1$MX$TmpRte6
OS/TTMP1$MX$TmpRte7
OS/TTMP1$MX$TmpRte8
ds_St_TMP | TransOpto temperatures alarms | OS/TTMP1$ST$Tmp1Alm
OS/TTMP1$ST$Tmp1Wrn
OS/TTMP1$ST$Tmp2Alm
OS/TTMP1$ST$Tmp2Wrn
OS/TTMP1$ST$Tmp3Alm
OS/TTMP1$ST$Tmp3Wrn
OS/TTMP1$ST$Tmp4Alm
OS/TTMP1$ST$Tmp4Wrn
OS/TTMP1$ST$Tmp5Alm
OS/TTMP1$ST$Tmp5Wrn
OS/TTMP1$ST$Tmp6Alm
OS/TTMP1$ST$Tmp6Wrn
OS/TTMP1$ST$Tmp7Alm
OS/TTMP1$ST$Tmp7Wrn
OS/TTMP1$ST$Tmp8Alm
OS/TTMP1$ST$Tmp8Wrn
OS/TTMP1$ST$TmpRte1Alm
OS/TTMP1$ST$TmpRte1Wrn
OS/TTMP1$ST$TmpRte2Alm
OS/TTMP1$ST$TmpRte2Wrn
OS/TTMP1$ST$TmpRte3Alm
OS/TTMP1$ST$TmpRte3Wrn
OS/TTMP1$ST$TmpRte4Alm
OS/TTMP1$ST$TmpRte4Wrn
OS/TTMP1$ST$TmpRte5Alm
OS/TTMP1$ST$TmpRte5Wrn
OS/TTMP1$ST$TmpRte6Alm
OS/TTMP1$ST$TmpRte6Wrn
OS/TTMP1$ST$TmpRte7Alm
OS/TTMP1$ST$TmpRte7Wrn
OS/TTMP1$ST$TmpRte8Alm
OS/TTMP1$ST$TmpRte8Wrn
ds_St_IO02 | Generic IO Alarms | OS/GGIO1$ST$AnIn1AlmH
OS/GGIO1$ST$AnIn1WrnH
OS/GGIO1$ST$AnIn1WrnL
OS/GGIO1$ST$AnIn1AlmL
OS/GGIO1$ST$AnIn2AlmH
OS/GGIO1$ST$AnIn2WrnH
OS/GGIO1$ST$AnIn2WrnL
OS/GGIO1$ST$AnIn2AlmL
OS/GGIO1$ST$AnIn3AlmH
OS/GGIO1$ST$AnIn3WrnH
OS/GGIO1$ST$AnIn3WrnL
OS/GGIO1$ST$AnIn3AlmL
OS/GGIO1$ST$AnIn4AlmH
OS/GGIO1$ST$AnIn4WrnH
OS/GGIO1$ST$AnIn4WrnL
OS/GGIO1$ST$AnIn4AlmL
OS/GGIO1$ST$AnIn5AlmH
OS/GGIO1$ST$AnIn5WrnH
OS/GGIO1$ST$AnIn5WrnL
OS/GGIO1$ST$AnIn5AlmL
OS/GGIO1$ST$AnIn6AlmH
OS/GGIO1$ST$AnIn6WrnH
OS/GGIO1$ST$AnIn6WrnL
OS/GGIO1$ST$AnIn6AlmL
OS/GGIO1$ST$DiTr1AlmH
OS/GGIO1$ST$DiTr1WrnH
OS/GGIO1$ST$DiTr2AlmH
OS/GGIO1$ST$DiTr2WrnH
OS/GGIO1$ST$DiTr3AlmH
OS/GGIO1$ST$DiTr3WrnH
ds_St_IO03 | Generic IO Alarms | OS/GGIO1$ST$AnIn7AlmH
OS/GGIO1$ST$AnIn7WrnH
OS/GGIO1$ST$AnIn7WrnL
OS/GGIO1$ST$AnIn7AlmL
OS/GGIO1$ST$AnIn8AlmH
OS/GGIO1$ST$AnIn8WrnH
OS/GGIO1$ST$AnIn8WrnL
OS/GGIO1$ST$AnIn8AlmL
OS/GGIO1$ST$AnIn9AlmH
OS/GGIO1$ST$AnIn9WrnH
OS/GGIO1$ST$AnIn9WrnL
OS/GGIO1$ST$AnIn9AlmL
OS/GGIO1$ST$AnIn10AlmH
OS/GGIO1$ST$AnIn10WrnH
OS/GGIO1$ST$AnIn10WrnL
OS/GGIO1$ST$AnIn10AlmL
OS/GGIO1$ST$AnIn11AlmH
OS/GGIO1$ST$AnIn11WrnH
OS/GGIO1$ST$AnIn11WrnL
OS/GGIO1$ST$AnIn11AlmL
OS/GGIO1$ST$AnIn12AlmH
OS/GGIO1$ST$AnIn12WrnH
OS/GGIO1$ST$AnIn12WrnL
OS/GGIO1$ST$AnIn12AlmL
OS/GGIO1$ST$DiTr4AlmH
OS/GGIO1$ST$DiTr4WrnH
OS/GGIO1$ST$DiTr5AlmH
OS/GGIO1$ST$DiTr5WrnH
OS/GGIO1$ST$DiTr6AlmH
OS/GGIO1$ST$DiTr6WrnH
ds_St_IO04 | Generic IO Alarms | OS/GGIO1$ST$AnIn13AlmH
OS/GGIO1$ST$AnIn13WrnH
OS/GGIO1$ST$AnIn13WrnL
OS/GGIO1$ST$AnIn13AlmL
OS/GGIO1$ST$AnIn14AlmH
OS/GGIO1$ST$AnIn14WrnH
OS/GGIO1$ST$AnIn14WrnL
OS/GGIO1$ST$AnIn14AlmL
OS/GGIO1$ST$AnIn15AlmH
OS/GGIO1$ST$AnIn15WrnH
OS/GGIO1$ST$AnIn15WrnL
OS/GGIO1$ST$AnIn15AlmL
OS/GGIO1$ST$AnIn16AlmH
OS/GGIO1$ST$AnIn16WrnH
OS/GGIO1$ST$AnIn16WrnL
OS/GGIO1$ST$AnIn16AlmL
OS/GGIO1$ST$AnIn17AlmH
OS/GGIO1$ST$AnIn17WrnH
OS/GGIO1$ST$AnIn17WrnL
OS/GGIO1$ST$AnIn17AlmL
OS/GGIO1$ST$AnIn18AlmH
OS/GGIO1$ST$AnIn18WrnH
OS/GGIO1$ST$AnIn18WrnL
OS/GGIO1$ST$AnIn18AlmL
OS/GGIO1$ST$DiTr7AlmH
OS/GGIO1$ST$DiTr7WrnH
OS/GGIO1$ST$DiTr8AlmH
OS/GGIO1$ST$DiTr8WrnH
OS/GGIO1$ST$DiTr9AlmH
OS/GGIO1$ST$DiTr9WrnH
ds_St_Bsh01 | Bushing status of channels 1-6 | BMT/ZBSH1$ST$React1AlmH
BMT/ZBSH1$ST$React1WrnH
BMT/ZBSH1$ST$React1WrnL
BMT/ZBSH1$ST$React1AlmL
BMT/ZBSH1$ST$React2AlmH
BMT/ZBSH1$ST$React2WrnH
BMT/ZBSH1$ST$React2WrnL
BMT/ZBSH1$ST$React2AlmL
BMT/ZBSH1$ST$React3AlmH
BMT/ZBSH1$ST$React3WrnH
BMT/ZBSH1$ST$React3WrnL
BMT/ZBSH1$ST$React3AlmL
BMT/ZBSH1$ST$React4AlmH
BMT/ZBSH1$ST$React4WrnH
BMT/ZBSH1$ST$React4WrnL
BMT/ZBSH1$ST$React4AlmL
BMT/ZBSH1$ST$React5AlmH
BMT/ZBSH1$ST$React5WrnH
BMT/ZBSH1$ST$React5WrnL
BMT/ZBSH1$ST$React5AlmL
BMT/ZBSH1$ST$React6AlmH
BMT/ZBSH1$ST$React6WrnH
BMT/ZBSH1$ST$React6WrnL
BMT/ZBSH1$ST$React6AlmL
ds_St_Bsh02 | Bushing status of channels 1-6 | BMT/ZBSH1$ST$LosSig1
BMT/ZBSH1$ST$LosSig2
BMT/ZBSH1$ST$LosSig3
BMT/ZBSH1$ST$LosSig4
BMT/ZBSH1$ST$LosSig5
BMT/ZBSH1$ST$LosSig6
BMT/ZBSH1$ST$LowSig1
BMT/ZBSH1$ST$LowSig2
BMT/ZBSH1$ST$LowSig3
BMT/ZBSH1$ST$LowSig4
BMT/ZBSH1$ST$LowSig5
BMT/ZBSH1$ST$LowSig6
BMT/ZBSH1$ST$SatSig1
BMT/ZBSH1$ST$SatSig2
BMT/ZBSH1$ST$SatSig3
BMT/ZBSH1$ST$SatSig4
BMT/ZBSH1$ST$SatSig5
BMT/ZBSH1$ST$SatSig6
BMT/ZBSH1$ST$NoiseSig1
BMT/ZBSH1$ST$NoiseSig2
BMT/ZBSH1$ST$NoiseSig3
ds_St_Bsh03 | Bushing status of channels 7-9 | BMT/ZBSH2$ST$React1AlmH
BMT/ZBSH2$ST$React1WrnH
BMT/ZBSH2$ST$React1WrnL
BMT/ZBSH2$ST$React1AlmL
BMT/ZBSH2$ST$React2AlmH
BMT/ZBSH2$ST$React2WrnH
BMT/ZBSH2$ST$React2WrnL
BMT/ZBSH2$ST$React2AlmL
BMT/ZBSH2$ST$React3AlmH
BMT/ZBSH2$ST$React3WrnH
BMT/ZBSH2$ST$React3WrnL
BMT/ZBSH2$ST$React3AlmL
BMT/ZBSH2$ST$LosSig1
BMT/ZBSH2$ST$LosSig2
BMT/ZBSH2$ST$LosSig3
BMT/ZBSH2$ST$LowSig1
BMT/ZBSH2$ST$LowSig2
BMT/ZBSH2$ST$LowSig3
BMT/ZBSH2$ST$SatSig1
BMT/ZBSH2$ST$SatSig2
BMT/ZBSH2$ST$SatSig3
ds_Mx_Bsh01 | Bushing measurements of channels 1-6 | BMT/ZBSH1$MX$LeakA1
BMT/ZBSH1$MX$LeakA2
BMT/ZBSH1$MX$LeakA3
BMT/ZBSH1$MX$LeakA4
BMT/ZBSH1$MX$LeakA5
BMT/ZBSH1$MX$LeakA6
BMT/ZBSH1$MX$React1
BMT/ZBSH1$MX$React2
BMT/ZBSH1$MX$React3
BMT/ZBSH1$MX$React4
BMT/ZBSH1$MX$React5
BMT/ZBSH1$MX$React6
ds_Mx_Bsh02 | Bushing measurements of channels 7-9 | BMT/ZBSH2$MX$LeakA1
BMT/ZBSH2$MX$LeakA2
BMT/ZBSH2$MX$LeakA3
BMT/ZBSH2$MX$React1
BMT/ZBSH2$MX$React2
BMT/ZBSH2$MX$React3
ds_Tmp | Temperature measurements and status | BMT/TTMP1$ST$Tmp1Fail
BMT/TTMP1$ST$Tmp2Fail
BMT/TTMP1$ST$Tmp3Fail
BMT/TTMP1$ST$Tmp4Fail
BMT/TTMP1$ST$Tmp5Fail
BMT/TTMP1$ST$Tmp1Wrn
BMT/TTMP1$ST$Tmp2Wrn
BMT/TTMP1$ST$Tmp3Wrn
BMT/TTMP1$ST$Tmp4Wrn
BMT/TTMP1$MX$Tmp1
BMT/TTMP1$MX$Tmp2
BMT/TTMP1$MX$Tmp3
BMT/TTMP1$MX$Tmp4
BMT/TTMP1$MX$Tmp5
BMT/TTMP1$MX$Tmp6
BMT/TTMP1$MX$Tmp7
BMT/TTMP1$MX$Tmp8
BMT/TTMP1$MX$Tmp9
BMT/TTMP1$MX$Tmp10
BMT/TTMP1$MX$Tmp11
ds_Pdc | Partial Discharge measurements and status of channels 1-3 | BMT/SPDC1$ST$PdMax1AlmH
BMT/SPDC1$ST$PdMax1WrnH
BMT/SPDC1$ST$PdMax2AlmH
BMT/SPDC1$ST$PdMax2WrnH
BMT/SPDC1$ST$PdMax3AlmH
BMT/SPDC1$ST$PdMax3WrnH
BMT/SPDC1$MX$PdIdx1
BMT/SPDC1$MX$PdIdx2
BMT/SPDC1$MX$PdIdx3
BMT/SPDC1$MX$PdIdxN1
BMT/SPDC1$MX$PdIdxN2
BMT/SPDC1$MX$PdIdxN3
BMT/SPDC1$MX$PdCnt1
BMT/SPDC1$MX$PdCnt2
BMT/SPDC1$MX$PdCnt3
BMT/SPDC1$MX$PdCntN1
BMT/SPDC1$MX$PdCntN2
BMT/SPDC1$MX$PdCntN3
BMT/SPDC1$MX$PdVal1
BMT/SPDC1$MX$PdVal2
BMT/SPDC1$MX$PdVal3
BMT/SPDC1$MX$PdValN1
BMT/SPDC1$MX$PdValN2
BMT/SPDC1$MX$PdValN3
BMT/SPDC1$MX$PdMax1
BMT/SPDC1$MX$PdMax2
BMT/SPDC1$MX$PdMax3
BMT/SPDC1$MX$PdMaxN1
BMT/SPDC1$MX$PdMaxN2
BMT/SPDC1$MX$PdMaxN3
BMT/SPDC1$MX$Noise1
BMT/SPDC1$MX$Noise2
BMT/SPDC1$MX$Noise3
ds_St_PP01 | Polar plots and phase angles status of Channels 1-6 | BMT/GGIO2$ST$FrqWrn
BMT/GGIO2$ST$Phd12AlmH
BMT/GGIO2$ST$Phd12WrnH
BMT/GGIO2$ST$Phd13AlmH
BMT/GGIO2$ST$Phd13WrnH
BMT/GGIO2$ST$Phd45AlmH
BMT/GGIO2$ST$Phd45WrnH
BMT/GGIO2$ST$Phd46AlmH
BMT/GGIO2$ST$Phd46WrnH
BMT/GGIO2$ST$ReactPAlmH
BMT/GGIO2$ST$ReactPWrnH
BMT/GGIO2$ST$LosFactPAlmH
BMT/GGIO2$ST$LosFactPWrnH
BMT/GGIO2$ST$ReactSAlmH
BMT/GGIO2$ST$ReactSWrnH
BMT/GGIO2$ST$LosFactSAlmH
BMT/GGIO2$ST$LosFactSWrnH
BMT/GGIO2$ST$PdIdxPAlmH
BMT/GGIO2$ST$PdIdxPWrnH
BMT/GGIO2$ST$PdCntPAlmH
BMT/GGIO2$ST$PdCntPWrnH
BMT/GGIO2$ST$PdValPAlmH
BMT/GGIO2$ST$PdValPWrnH
BMT/GGIO2$ST$LowBshAlm
BMT/GGIO2$ST$LowFrqAlm
ds_St_PP02 | Polar plots and phase angles status of Channels 7-9 | BMT/GGIO3$ST$Phd12AlmH
BMT/GGIO3$ST$Phd12WrnH
BMT/GGIO3$ST$Phd13AlmH
BMT/GGIO3$ST$Phd13WrnH
BMT/GGIO3$ST$ReactPAlmH
BMT/GGIO3$ST$ReactPWrnH
BMT/GGIO3$ST$LosFactPAlmH
BMT/GGIO3$ST$LosFactPWrnH
ds_Mx_PP01 | Polar plots and phase angle measurements of Channels 1-6 | BMT/GGIO2$MX$Frequency
BMT/GGIO2$MX$Phs12
BMT/GGIO2$MX$Phs13
BMT/GGIO2$MX$Phs45
BMT/GGIO2$MX$Phs46
BMT/GGIO2$MX$Phd12
BMT/GGIO2$MX$Phd13
BMT/GGIO2$MX$Phd45
BMT/GGIO2$MX$Phd46
BMT/GGIO2$MX$React1
BMT/GGIO2$MX$React2
BMT/GGIO2$MX$React3
BMT/GGIO2$MX$React4
BMT/GGIO2$MX$React5
BMT/GGIO2$MX$React6
BMT/GGIO2$MX$ReactP
BMT/GGIO2$MX$LosFactP
BMT/GGIO2$MX$ReactS
BMT/GGIO2$MX$LosFactS
BMT/GGIO2$MX$FrqThd
BMT/GGIO2$MX$FrqHys
BMT/GGIO2$MX$Tmp1
BMT/GGIO2$MX$Tmp2
BMT/GGIO2$MX$Tmp3
BMT/GGIO2$MX$LowSigThd
BMT/GGIO2$MX$Hum
ds_Mx_PP02 | Polar plots and phase angle measurements of Channels 7-9 | BMT/GGIO3$MX$Frequency
BMT/GGIO3$MX$Phs12
BMT/GGIO3$MX$Phs13
BMT/GGIO3$MX$Phd12
BMT/GGIO3$MX$Phd13
BMT/GGIO3$MX$React1
BMT/GGIO3$MX$React2
BMT/GGIO3$MX$React3
BMT/GGIO3$MX$ReactP
BMT/GGIO3$MX$LosFactP
ds_St_CB01 | Cooling bank status | MO/GGIO4$ST$Alm1
MO/GGIO4$ST$Alm2
MO/GGIO4$ST$Alm3
MO/GGIO4$ST$Alm4
MO/GGIO4$ST$Wrn1
MO/GGIO4$ST$Wrn2
MO/GGIO4$ST$Wrn3
MO/GGIO4$ST$Wrn4
MO/GGIO4$ST$Alm5
MO/GGIO4$ST$Alm6
MO/GGIO4$ST$Alm7
MO/GGIO4$ST$Alm8
MO/GGIO4$ST$Alm9
MO/GGIO4$ST$Alm10
MO/GGIO4$ST$Alm11
MO/GGIO4$ST$Alm12
MO/GGIO4$ST$Alm13
MO/GGIO4$ST$Alm14
MO/GGIO4$ST$Wrn5
MO/GGIO4$ST$Ind1
MO/GGIO4$ST$Ind2
MO/GGIO4$ST$Ind3
MO/GGIO4$ST$Ind4
ds_St_CB02 | Cooling Bank Values | MO/GGIO4$ST$IntIn1
MO/GGIO4$ST$IntIn2
MO/GGIO4$ST$IntIn3
MO/GGIO4$ST$IntIn4
MO/GGIO4$ST$IntIn5
MO/GGIO4$ST$IntIn6
MO/GGIO4$ST$IntIn7
MO/GGIO4$ST$IntIn8
MO/GGIO4$ST$IntIn9
MO/GGIO4$ST$IntIn10
MO/GGIO4$ST$IntIn11
MO/GGIO4$ST$IntIn12
MO/GGIO4$ST$IntIn13
MO/GGIO4$ST$IntIn14
MO/GGIO4$ST$IntIn15
MO/GGIO4$ST$IntIn16
MO/GGIO4$ST$IntIn17
MO/GGIO4$ST$IntIn18
MO/GGIO4$ST$IntIn19
MO/GGIO4$ST$IntIn20
MO/GGIO4$ST$IntIn21
MO/GGIO4$ST$IntIn22
MO/GGIO4$ST$IntIn23
MO/GGIO4$ST$IntIn24
MO/GGIO4$ST$IntIn25
MO/GGIO4$ST$IntIn26
MO/GGIO4$MX$AnIn1
ds_Mx_Phases | Transformer phase measurements | MO/MMXU1$MX$VA
MO/MMXU1$MX$MaxVA
MO/MMXU1$MX$ImbA
MO/MMXU1$MX$ImbAvg
ds_St_TxSupv | Transformer Supervision Status | MO/SPTR1$ST$HPTmpAlm
MO/SPTR1$ST$HPTmpWrn
MO/SPTR1$ST$CdsTmpAlm
MO/SPTR1$ST$CdsTmpWrn
MO/SPTR1$ST$BubTmpAlm
MO/SPTR1$ST$BubTmpWrn
MO/SPTR1$ST$MstAlm
MO/SPTR1$ST$MstWrn
ds_Mx_TxSupv | Transformer Supervision Measured values | MO/SPTR1$MX$HPTmpClc1
MO/SPTR1$MX$HPTmpClc2
MO/SPTR1$MX$HPTmpClc3
MO/SPTR1$MX$HPTmpMax
MO/SPTR1$MX$Mst
MO/SPTR1$MX$CdsTmp
MO/SPTR1$MX$MstPap
MO/SPTR1$MX$BubTmp
MO/SPTR1$MX$BubTmpMar
MO/SPTR1$MX$InsTmms1
MO/SPTR1$MX$MstBar
MO/SPTR1$MX$AgeRte1
MO/SPTR1$MX$AgeRte2
MO/SPTR1$MX$AgeRte3
MO/SPTR1$MX$AgeRte4
MO/SPTR1$ST$InsTmms2
MO/SPTR1$ST$ServTm
ds_TxLoad | Tranformer load parameters | MO/YPTR1$ST$OvlTm1
MO/YPTR1$ST$OvlFact1
MO/YPTR1$ST$OvlTm2
MO/YPTR1$ST$OvlFact2
MO/YPTR1$ST$OvlTm3
MO/YPTR1$ST$OvlFact3
MO/YPTR1$ST$OvlTm4
MO/YPTR1$ST$OvlFact4
MO/YPTR1$ST$OvlTm5
MO/YPTR1$ST$OvlFact5
MO/YPTR1$ST$OvlTm6
MO/YPTR1$ST$OvlFact6
MO/YPTR1$ST$OvlTm7
MO/YPTR1$ST$OvlFact7
MO/YPTR1$ST$OvlTm8
MO/YPTR1$ST$OvlFact8
MO/YPTR1$ST$OvlTm9
MO/YPTR1$ST$OvlFact9
MO/YPTR1$ST$OvlTm10
MO/YPTR1$ST$OvlFact10
MO/YPTR1$MX$OvlVal1
MO/YPTR1$MX$OvlVal2
MO/YPTR1$MX$OvlVal3
MO/YPTR1$MX$OvlVal4
MO/YPTR1$MX$OvlVal5
MO/YPTR1$MX$OvlVal6
MO/YPTR1$MX$OvlVal7
MO/YPTR1$MX$OvlVal8
MO/YPTR1$MX$OvlVal9
MO/YPTR1$MX$OvlVal10
ds_St_OLTC | Transformer On Load Tap Changer Status | MO/SLTC1$ST$Tmp1Alm
MO/SLTC1$ST$Tmp1Wrn
MO/SLTC1$ST$Tmp2Alm
MO/SLTC1$ST$Tmp2Wrn
MO/SLTC1$ST$OpRte1Alm
MO/SLTC1$ST$OpRte1Wrn
MO/SLTC1$ST$OpRte2Alm
MO/SLTC1$ST$OpRte2Wrn
MO/SLTC1$ST$TorqTm1Alm
MO/SLTC1$ST$TorqTm1Wrn
MO/SLTC1$ST$TorqTm2Alm
MO/SLTC1$ST$TorqTm2Wrn
MO/SLTC1$ST$Torq1Alm
MO/SLTC1$ST$Torq1Wrn
MO/SLTC1$ST$Torq2Alm
MO/SLTC1$ST$Torq2Wrn
MO/SLTC1$ST$Torq3Alm
MO/SLTC1$ST$Torq3Wrn
MO/SLTC1$ST$TorqAvgAlm
MO/SLTC1$ST$TorqAvgWrn
ds_Mx_OLTC | Transformer On Load Tap Changer Measurements | MO/SLTC1$MX$Tmp1
MO/SLTC1$MX$Tmp2
MO/SLTC1$MX$TorqTm1
MO/SLTC1$MX$TorqTm2
MO/SLTC1$MX$Torq1
MO/SLTC1$MX$Torq2
MO/SLTC1$MX$Torq3
MO/SLTC1$MX$TorqAvg
MO/SLTC1$MX$TorqTmPct1
MO/SLTC1$MX$TorqTmPct2
MO/SLTC1$MX$TorqPct1
MO/SLTC1$MX$TorqPct2
MO/SLTC1$MX$TorqPct3
MO/SLTC1$MX$TorqPctAvg
MO/SLTC1$ST$OpRte1
MO/SLTC1$ST$OpRte2
MO/YLTC1$ST$OpCnt1
MO/YLTC1$ST$OpCnt2
MO/YLTC1$ST$OpTm
MO/YLTC1$ST$TapPos1
MO/YLTC1$ST$TapPos2
MO/YLTC1$ST$TapPos3
MO/YLTC1$ST$TapPos4
MO/YLTC1$ST$TapPos5
MO/YLTC1$ST$TapPosGr

## IEC61850 Reports
Report Control Name | Report Parameter | Value
urcb_Mx_Gas_OS1 | desc | Oil Source Dissolved Gas and Moisture Concentrations (ppm)
| datSet | ds_Mx_Gas_OS1
| rptID | OS.urcb_Mx_Gas_OS1
| intgPd | 60000
| max | 1
urcb_Mx_GasRoC_OS1 | desc | Oil Source Rate of change of Gas Concentrations (ppm/day)
| datSet | ds_Mx_GasRoC_OS1
| rptID | OS.urcb_Mx_GasRoC_OS1
| intgPd | 60000
| max | 1
urcb_St_Gas_OS1 | desc | Oil Souce Alarm Status of Gas Concentrations
| datSet | ds_St_Gas_OS1
| rptID | OS.urcb_St_Gas_OS1
| intgPd | 60000
| max | 1
urcb_St_GasRoC_OS1 | desc | Oil Source Alarm status of Rate of change of Gas Concentrations
| datSet | ds_St_GasRoC_OS1
| rptID | OS.urcb_St_GasRoC_OS1
| intgPd | 60000
| max | 1
urcb_St_GasRatio_OS1 | desc | Oil Souce Alarm status of Ratios of Gas Concentration
| datSet | ds_St_GasRatio_OS1
| rptID | OS.urcb_St_GasRatio_OS1
| intgPd | 60000
| max | 1
urcb_St_IO01 | desc | Generic IO Alarms
| datSet | ds_St_IO01
| rptID | OS.urcb_St_IO01
| intgPd | 60000
| max | 1
urcb_Mx_IO | desc | Generic IO measurements
| datSet | ds_Mx_IO
| rptID | OS.urcb_Mx_IO
| intgPd | 60000
| max | 1
urcb_Mx_TMP | desc | TransOpto temperature measurements
| datSet | ds_Mx_TMP
| rptID | OS.urcb_Mx_TMP
| intgPd | 60000
| max | 1
urcb_St_TMP | desc | TransOpto temperatures alarms
| datSet | ds_St_TMP
| rptID | OS.urcb_St_TMP
| intgPd | 60000
| max | 1
urcb_St_IO02 | desc | Generic IO Alarms
| datSet | ds_St_IO02
| rptID | OS.urcb_St_IO02
| intgPd | 60000
| max | 1
urcb_St_IO03 | desc | Generic IO Alarms
| datSet | ds_St_IO03
| rptID | OS.urcb_St_IO03
| intgPd | 60000
| max | 1
urcb_St_IO04 | desc | Generic IO Alarms
| datSet | ds_St_IO04
| rptID | OS.urcb_St_IO04
| intgPd | 60000
| max | 1
urcb_St_Bsh01 | desc | Bushing status of channels 1-6
| datSet | ds_St_Bsh01
| rptID | BMT.urcb_St_Bsh01
| intgPd | 60000
| max | 1
urcb_St_Bsh02 | desc | Bushing status of channels 1-6
| datSet | ds_St_Bsh02
| rptID | BMT.urcb_St_Bsh02
| intgPd | 60000
| max | 1
urcb_St_Bsh03 | desc | Bushing status of channels 7-9
| datSet | ds_St_Bsh03
| rptID | BMT.urcb_St_Bsh03
| intgPd | 60000
| max | 1
urcb_Mx_Bsh01 | desc | Bushing measurements of channels 1-6
| datSet | ds_Mx_Bsh01
| rptID | BMT.urcb_Mx_Bsh01
| intgPd | 60000
| max | 1
urcb_Mx_Bsh02 | desc | Bushing measurements of channels 7-9
| datSet | ds_Mx_Bsh02
| rptID | BMT.urcb_Mx_Bsh02
| intgPd | 60000
| max | 1
urcb_Tmp | desc | Temperature measurements and status
| datSet | ds_Tmp
| rptID | BMT.urcb_Tmp
| intgPd | 60000
| max | 1
urcb_Pdc | desc | Partial Discharge measurements and status of channels 1-3
| datSet | ds_Pdc
| rptID | BMT.urcb_Pdc
| intgPd | 60000
| max | 1
urcb_St_PP01 | desc | Polar plots and phase angle status of Channels 1-6
| datSet | ds_St_PP01
| rptID | BMT.urcb_St_PP01
| intgPd | 60000
| max | 1
urcb_St_PP02 | desc | Polar plots and phase angle status of Channels 7-9
| datSet | ds_St_PP02
| rptID | BMT.urcb_St_PP02
| intgPd | 60000
| max | 1
urcb_Mx_PP01 | desc | Polar plots and phase angle measurements of Channels 1-6
| datSet | ds_Mx_PP01
| rptID | BMT.urcb_Mx_PP01
| intgPd | 60000
| max | 1
urcb_Mx_PP02 | desc | Polar plots and phase angle measurements of Channels 7-9
| datSet | ds_Mx_PP02
| rptID | BMT.urcb_Mx_PP02
| intgPd | 60000
| max | 1
urcb_St_CB01 | desc | Cooling bank status
| datSet | ds_St_CB01
| rptID | MO.urcb_St_CB01
| intgPd | 60000
| max | 1
urcb_St_CB02 | desc | Cooling Bank Values
| datSet | ds_St_CB02
| rptID | MO.urcb_St_CB02
| intgPd | 60000
| max | 1
urcb_Mx_Phases | desc | Transformer phase measurements
| datSet | ds_Mx_Phases
| rptID | MO.urcb_Mx_Phases
| intgPd | 60000
| max | 1
urcb_St_TxSupv | desc | Transformer Supervision Status
| datSet | ds_St_TxSupv
| rptID | MO.urcb_St_TxSupv
| intgPd | 60000
| max | 1
urcb_Mx_TxSupv | desc | Transformer Supervision Measurement values
| datSet | ds_Mx_TxSupv
| rptID | MO.urcb_Mx_TxSupv
| intgPd | 60000
| max | 1
urcb_TxLoad | desc | Tranformer load parameters
| datSet | ds_TxLoad
| rptID | MO.urcb_TxLoad
| intgPd | 60000
| max | 1
urcb_St_OLTC | desc | Transformer On Load Tap Changer Status
| datSet | ds_St_OLTC
| rptID | MO.urcb_St_OLTC
| intgPd | 60000
| max | 1
urcb_Mx_OLTC | desc | Transformer On Load Tap Changer Measurements
| datSet | ds_Mx_OLTC
| rptID | MO.urcb_Mx_OLTC
| intgPd | 60000
| max | 1